## PARAMETERS INPUT
|  | THERMODYNAMIC MODULE | [27 empty] | ECONOMIC | [91 empty] | OUTPUT | [76 empty] | OUTPUT
|  | GT INPUT | [11 empty] | HRSG INPUT | [6 empty] | SAC INPUT | [8 empty] | Number of period | Interest rate | GT |  | HRSG |  | SAC |  | Cost of fuel | [6 empty] | Assume temperature of combustion product=900 | [19 empty] | Temperature profile of HRSG | [15 empty] | EXERGY 13 STREAMS | [93 empty] | INEFFICIENCIES COST OF GT |  |  |  | INEFFICIENCIES COST OF HRSG |  |  |  | Inefficiencies cost of SAC |  |  |  | GT |  |  |  | HRSG |  |  |  | SAC
|  | Operating hours | Capacity of GT | Lower Heating Value | Compressor inlet temperature | Compressor pressure ratio | Compressor isentropic efficiency | Specific heat ratio of air | Specific heat ratio of gas | Turbine isentropic efficiency | Mass flow of fuel | Mass flow of air | Power | Operating hours | Heat loss factor | Blowdown factor | Exhaust heat temperature | Mass flow of feed water | Steam temperature | Steam flow | Operating hours | Capacity of SAC | Steam supply | Chilled water generated | Chilled water flow | Temperature of chilled water out | Temperature of chilled water return | Temperature of cooling water out | Temperature of cooling water return |  |  | Capital Cost of GT | O&M cost of GT | Capital Cost of HRSG | O&M cost of HRSG | Capital Cost of SAC | O&M cost of SAC |  | T2(cooling water) | T1(steam) | TR(chw) | Mass flow rate of ex heat to HRSG | T02 | Cpa | Wcomp | Temp. of combustion product | Cpg | Cpg (T04-T05) | (T04-T05) | T04 | T05 | T05 | Wturb | Power generated | Mass flow rate of fuel | Mass flow rate of fuel | Mass flow rate of chw | Mass flow rate of feed water in HRSG | heatloss factor | blowdown factor | Temperature of Tw1 in Celcius | Temperature of Tw2 in Celcius | Temperature of steam in Kelvin | Temperature of exhaust heat in Kelvin (Tg1) | h@Ts | h@Tw1(fluid) | h@Tw2(fluid) | h@Tw2 (vapour) | Cpg(econ) | Economizer duty | Gas Temperature drop | Cpg (evap@Tg1) | Cpg (Tg1-Tg3) | Tg1-Tg2 | Tg2 | Tw2 | Tg3 | Tg1-Tg3 | h@Ts | h@SAC drain | ξ | E1(act) | E1 (theory) | T3 | T3 (theory) | Cpg | Cpg (theory) | E3(act) | E3 (theory) | T4 | T4 /T5 (theory) | m4 | Cpg | Cpg (theory) | To | E4(act) | E4 (theory) | T5 | m5 | Cpg | To | E5(act) | E5 (teory) | E6(act) | E6 (theory) | m7 | T7 | h7 | ho | S7 | So | E7(act) | E7 (theory) | m8 | T8 (actual) | T8 (theory) | Cpg | Cpg (theory) | To | E8(act) | E8 (theory) | m9 | T9 | h9 | S9 | E9(act) | E9 (theory) | m10 | h10 | S10 | E10(act) | E10 (theory) | m11 | T11 | h11 | S11 | E11(act) | E11 (theory) | m12 | h12 | S12 | E12(act) | E12 (theory) | m13 | h13 | S13 | E13(act) | E13 (theory) | Exergy Destruction of GT (act) | Exergy Destruction of GT (MODEL) | Exergy Destruction of HRSG (act) | Exergy Destruction of HRSG (MODEL) | Exergy Destruction of SAC (model) | Exergy Destruction of SAC (MODEL) | CRF | ZGT | ZGT | ZGT | ZHRSG | ZHRSG | ZHRSG | ZSAC | ZSAC | ZSAC | True cost of power (act) | True cost of power (act) | True cost of power (model) | True cost of power (model) | True cost of chilled water(act) | True cost of chilled water(act) | True cost of chilled water(act) | True cost of chilled water(model) | True cost of chilled water(model) | True cost of chilled water(model) | Inefficiencies cost of GT (act) | Inefficiencies cost of GT (model) | Inefficiencies cost of GT(act) | Inefficiencies cost of GT(model) | Inefficiencies cost of HRSG(act) | Inefficiencies cost of HRSG (model) | Inefficiencies cost of HRSG(act) | Inefficiencies cost of HRSG (model) | Inefficiencies cost of SAC (act) | Inefficiencies cost of SAC (model) | Inefficiencies cost of SAC(act) | Inefficiencies cost of SAC(model) | Exergy rate of fuel (act) | Exergy rate of fuel (Model) | Exergy rate of product (act) | Exergy rate of product (Model) | Exergy rate of fuel (act) | Exergy rate of fuel (Model) | Exergy rate of product (act) | Exergy rate of product (Model) | Exergy rate of fuel (act) | Exergy rate of fuel (Model) | Exergy rate of product (act) | Exergy rate of product (Model) | Mass flow rate of exhaust heat generated | Actual Power generated | Model Power generated | Actual mass flow rate of steam generated | Model mass flow rate of steam generated | Actual mass flw rate ofchilled water generated | Model mass flow rate of chilled water generated | Energy efficiency of GT (actual) | Energy efficiency of GT (model) | Energy efficiency of HRSG (actual) | Energy efficiency of HRSG (model) | COP of SAC (act) | COP of SAC (model) | Exergetic efficiency of GT (actual) | Exergetic efficiency of GT (model) | Exergetic efficiency of HRSG (actual) | Exergetic efficiency of HRSG (model) | Exergetic efficiency of SAC (model) | Exergetic efficiency of SAC (actual) | Estimated cost of power | Estimated cost of chilled water | TOTAL Inefficiencies cost (ACT) | TOTAL Inefficiencies cost (MODEL)
DATE | DAYS | hours | MW | kJ/kg | K |  | % |  |  | % | M3 | kg/s | kW | hours | (%) | (%) | Deg C | T | Deg C | T/h | hours | RT | kg | RTh | M3/h | Deg C | Deg C | Deg C | Deg C | Year | (%) | RM | RM/year | RM | RM/year | RM | RM/year | RM/GJ | K | K | K | kg/s | K |  | kW | K |  |  |  | K | C | K | kW | kW/h | M3/h | kg/s | M3/h | (kg/s) |  |  | (Celcius) | (Celcius) | (Kelvin) | (Kelvin) | [9 empty] | (Kelvin) | (Kelvin) | (Kelvin) | (Kelvin) | (Kelvin) | (RTh) | (RTh) |  | (MW) |  | (Kelvin) | (Kelvin) |  |  | (MW) |  | (Kelvin) | (Kelvin) | (kg/s) |  |  | (Kelvin) | (MW) |  | (Kelvin) | (kg/s) |  | (Kelvin) | (MW) |  | (MW) |  | (kg/s) | Deg C | (kJ/kg) | (kJ/kg) | (kJ/kg) | (kJ/kg) | (MW) |  | (kg/s) | (Kelvin) | (Kelvin) | (kJ/kg) | (kJ/kg) | (kJ/kg) | (MW) |  | (kg/s) | (Kelvin) | (kJ/kg) | (kJ/kg) | (MW) |  | (kg/s) | (kJ/kg) | (kJ/kg) | (MW) |  | (kg/s) | (Deg C) | (kJ/kg) | (kJ/kg) | (MW) |  | (kg/s) | (kJ/kg) | (kJ/kg) | (MW) |  | (kg/s) | (kJ/kg) | (kJ/kg) | (MW) |  | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) |  | RM | RM/s | RM/h | RM | RM/s | RM/h | RM/s | RM | RM/h | (RM/GJ) | (RM/kWh) | (RM/GJ) | (RM/kWh) | (RM/GJ) | (RM/kWh) | (RM/RTh) | (RM/GJ) | (RM/kWh) | (RM/RTh) | (RM/s) | (RM/s) | (RM/h) | (RM/h) | (RM/s) | (RM/s) | (RM/h) | (RM/h) | (RM/s) | (RM/s) | (RM/h) | (RM/h) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (kg/s) | kW | kW | (kg/s) | (kg/s) | (kg/s) | (kg/s) | (%) | (%) | (%) | (%) | (-) | (-) | (%) | (%) | (%) | (%) | (%) | (%) | (RM/kWh) | (RM/RTh) | (RM/h) | (RM/h)
2013-01-02 | 1 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 32812.0903 | 19 | 74208.8508 | 17 | 2 | 5 | 408.6892 | 94.5809 | 180 | 3.7358 | 17 | 1250 | 89762.0015 | 10064.5783 | 313.9228 | 9.6688 | 12.9771 | 37 | 30.0356 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 6.9644 | 180 | 3.3083 | 12.7183 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0842 | 520.1784 | 1251.3731 | 458.1947 | 731.1947 | 11879.0589 | 3092.0355 | 1367.1704 | 0.27013 | 18.466 | 26.2725 | 0.02 | 0.05 | 30 | 165 | 453 | 681.6892 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 615.3905 | 30.3853 | 1.1266 | 1.0222 | 258.1947 | 473 | 438 | 442.6147 | 239.0745 | 0.2189 | 0.027 | 1.06 | 14.3214 | 14.3214 | 681.6892 | 731.1947 | 1.1266 | 1.14 | 2.9737 | 3.6373 | 681.6892 | 731.1947 | 12.8339 | 1.1266 | 1.14 | 298.15 | 1.9805 | 2.4224 | 681.6892 | 6.4362 | 1.1266 | 298.15 | 0.99321 | 1.2149 | 3.092 | 5.0152 | 26.2725 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.098965 | 0.098965 | 12.8339 | 435 | 442.6147 | 1.0628 | 1.0651 | 298.15 | 0.3304 | 0.3645 | 1.0377 | 453 | 2816.5993 | 6.5855 | 0.89013 | 1.3939 | 21.47 | 125.7866 | 0.42541 | 0.077339 | 0.077339 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 87.8984 | 40.5492 | 0.1414 | 0.26726 | 0.86773 | 87.8984 | 54.395 | 0.18754 | 0.27528 | 0.89376 | 8.2556 | 5.6689 | 0.85892 | 0.76298 | 0.89402 | 1.4158 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 63.7909 | 0.22965 | 37.4228 | 0.13472 | 10.5622 | 0.038024 | 0.1337 | 11.8554 | 0.042679 | 0.15007 | 0.11894 | 0.081671 | 428.1801 | 294.0168 | 0.0082414 | 0.0073208 | 29.6689 | 26.355 | 0.017891 | 0.021589 | 64.4077 | 77.7213 | 11.3477 | 10.6841 | 3.092 | 6.1457 | 1.616 | 2.0579 | 0.79116 | 1.295 | 0.89013 | 1.3939 | 0.26726 | 0.86773 | 19.2701 | 3092.0355 | 5015.206 | 1.0377 | 1.6251 | 87.8984 | 285.3829 | 0.22886 | 0.3712 | 0.20637 | 0.32317 | 0.58429 | 0.86987 | 0.2159 | 0.35019 | 0.47947 | 0.62925 | 0.62251 | 0.30025 | 0.13472 | 0.15007 | 522.2566 | 398.0931
2013-01-04 | 2 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 26632.9129 | 19 | 74652.8519 | 17 | 2 | 5 | 404.5658 | 84.8071 | 180 | 3.3435 | 17 | 1250 | 61873.3639 | 6478.9247 | 197.0053 | 11.2274 | 13.5005 | 37 | 28.6009 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 8.3991 | 180 | 2.2731 | 12.6847 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0728 | 474.3929 | 1141.2287 |  | 666.8357 | 10804.8786 | 3110.5355 | 1109.7047 | 0.21926 | 11.5885 | 23.5575 | 0.02 | 0.05 | 30 | 165 | 453 | 677.5658 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 550.7736 | 27.2668 | 1.1255 | 1.0209 | 193.8357 | 473 | 438 | 445.7332 | 231.8325 | 0.2189 | 0.027 | 1.06 | 11.6244 | 11.6244 | 677.5658 | 666.8357 | 1.1255 | 1.1226 | 2.9129 | 2.7766 | 677.5658 | 666.8357 | 12.8 | 1.1255 | 1.1226 | 298.15 | 1.94 | 1.8492 | 677.5658 | 6.4192 | 1.1255 | 298.15 | 0.9729 | 0.92738 | 3.1105 | 3.941 | 23.5575 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.088738 | 0.088738 | 12.8 | 435 | 445.7332 | 1.0625 | 1.0659 | 298.15 | 0.32946 | 0.37778 | 0.92876 | 453 | 2816.5993 | 6.5855 | 0.79666 | 1.0427 | 21.47 | 119.7823 | 0.4054 | 0.07649 | 0.07649 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 55.1615 | 47.0722 | 0.16314 | 0.17009 | 0.86514 | 55.1615 | 56.5853 | 0.19483 | 0.17355 | 0.88272 | 5.601 | 4.9068 | 0.90258 | 0.51748 | 0.79515 | 1.0553 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 51.2016 | 0.18433 | 40.9101 | 0.14728 | 8.1361 | 0.02929 | 0.10299 | 9.9951 | 0.035982 | 0.12652 | 0.080693 | 0.070692 | 290.4953 | 254.4901 | 0.0086603 | 0.0049653 | 31.1771 | 17.8751 | 0.017357 | 0.015618 | 62.4846 | 56.2263 | 8.7115 | 8.8478 | 3.1105 | 3.6966 | 1.5622 | 1.4714 | 0.70792 | 0.95394 | 0.79666 | 1.0427 | 0.17009 | 0.86514 | 19.2193 | 3110.5355 | 3941.0258 | 0.92876 | 1.2156 | 55.1615 | 280.565 | 0.28364 | 0.35937 | 0.22748 | 0.29773 | 0.54566 | 0.35374 | 0.26759 | 0.33903 | 0.43957 | 0.64831 | 0.82973 | 0.21351 | 0.14728 | 0.12652 | 384.157 | 328.5915
2013-01-06 | 3 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 26865.007 | 19 | 74790.8983 | 17 | 2 | 5 | 395.3936 | 96.5439 | 180 | 3.8404 | 17 | 1250 | 90952.7877 | 9465.6284 | 329.2242 | 12.4198 | 15.99 | 37 | 30.0501 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 6.9499 | 180 | 3.5702 | 12.686 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0732 | 476.117 | 1145.3763 |  | 669.2593 | 10845.2256 | 3116.2874 | 1119.3753 | 0.22117 | 19.3661 | 26.8177 | 0.02 | 0.05 | 30 | 165 | 453 | 668.3936 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 632.6253 | 31.3158 | 1.123 | 1.02 | 196.2593 | 473 | 438 | 441.6842 | 226.7094 | 0.2189 | 0.027 | 1.06 | 11.7257 | 11.7257 | 668.3936 | 669.2593 | 1.123 | 1.1233 | 2.7965 | 2.8074 | 668.3936 | 669.2593 | 12.8013 | 1.123 | 1.1233 | 298.15 | 1.8625 | 1.8698 | 668.3936 | 6.4199 | 1.123 | 298.15 | 0.93403 | 0.93768 | 3.1163 | 3.9814 | 26.8177 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.10102 | 0.10102 | 12.8013 | 435 | 441.6842 | 1.0628 | 1.0649 | 298.15 | 0.32958 | 0.35936 | 1.0668 | 453 | 2816.5993 | 6.5855 | 0.91506 | 1.0535 | 21.47 | 125.8476 | 0.42561 | 0.077348 | 0.077348 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 92.1828 | 52.0626 | 0.17976 | 0.28728 | 0.59126 | 92.1828 | 67.0044 | 0.22955 | 0.29636 | 0.60994 | 5.8129 | 4.9369 | 0.71884 | 0.5579 | 0.92002 | 1.0681 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 52.1134 | 0.18761 | 40.7504 | 0.1467 | 9.1285 | 0.032862 | 0.11555 | 9.8495 | 0.035458 | 0.12468 | 0.083746 | 0.071125 | 301.4862 | 256.0511 | 0.0068974 | 0.0053531 | 24.8305 | 19.2711 | 0.016623 | 0.016251 | 59.8426 | 58.5031 | 8.9292 | 8.9182 | 3.1163 | 4.0011 | 1.5031 | 1.5104 | 0.81404 | 0.95249 | 0.91506 | 1.0535 | 0.28728 | 0.59126 | 19.2212 | 3116.2874 | 3981.3727 | 1.0668 | 1.2282 | 92.1828 | 189.7246 | 0.28171 | 0.35992 | 0.25903 | 0.29823 | 0.54232 | 1.0156 | 0.26577 | 0.33954 | 0.53105 | 0.63063 | 0.56123 | 0.31395 | 0.1467 | 0.12468 | 386.1593 | 333.8253
2013-01-08 | 4 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 26476.5025 | 19 | 71813.2056 | 17 | 2 | 5 | 396.6236 | 81.9893 | 180 | 3.2224 | 17 | 1250 | 92544.7005 | 11102.9186 | 359.6912 | 10.4863 | 13.6019 | 37 | 29.9436 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 7.0564 | 180 | 3.1156 | 12.6839 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0725 | 473.2308 | 1138.4331 |  | 665.2022 | 10777.6884 | 2992.2169 | 1103.1876 | 0.21797 | 21.1583 | 22.7748 | 0.02 | 0.05 | 30 | 165 | 453 | 669.6236 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 530.8262 | 26.281 | 1.1234 | 1.0193 | 192.2022 | 473 | 438 | 446.719 | 222.9046 | 0.2189 | 0.027 | 1.06 | 11.5561 | 11.5561 | 669.6236 | 665.2022 | 1.1234 | 1.1222 | 2.8116 | 2.7558 | 669.6236 | 665.2022 | 12.7992 | 1.1234 | 1.1222 | 298.15 | 1.8725 | 1.8354 | 669.6236 | 6.4188 | 1.1234 | 298.15 | 0.93907 | 0.92045 | 2.9922 | 3.9138 | 22.7748 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.08579 | 0.08579 | 12.7992 | 435 | 446.719 | 1.0625 | 1.0661 | 298.15 | 0.32942 | 0.3823 | 0.89512 | 453 | 2816.5993 | 6.5855 | 0.76781 | 1.0319 | 21.47 | 125.4019 | 0.42413 | 0.077285 | 0.077285 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 100.7135 | 43.9706 | 0.1528 | 0.3085 | 0.647 | 100.7135 | 57.0099 | 0.19625 | 0.31715 | 0.66515 | 5.7523 | 4.8864 | 0.86107 | 0.50703 | 0.77228 | 1.0458 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 53.3852 | 0.19219 | 41.0193 | 0.14767 | 9.1246 | 0.032848 | 0.1155 | 9.793 | 0.035255 | 0.12396 | 0.082873 | 0.070399 | 298.3444 | 253.4347 | 0.008262 | 0.004865 | 29.7433 | 17.5138 | 0.016766 | 0.015413 | 60.3563 | 55.4859 | 8.7445 | 8.8002 | 2.9922 | 3.8131 | 1.4902 | 1.4531 | 0.68202 | 0.94607 | 0.76781 | 1.0319 | 0.3085 | 0.647 | 19.218 | 2992.2169 | 3913.8356 | 0.89512 | 1.203 | 100.7135 | 211.223 | 0.27447 | 0.359 | 0.22053 | 0.29638 | 0.62519 | 0.75963 | 0.25893 | 0.33868 | 0.44198 | 0.65107 | 0.62702 | 0.40179 | 0.14767 | 0.12396 | 388.444 | 326.4344
2013-01-09 | 5 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 26658.2103 | 19 | 73349.7944 | 17 | 2 | 5 | 403.8837 | 91.5343 | 180 | 3.7415 | 17 | 1250 | 83185.8942 | 9670.1585 | 306.2921 | 10.1545 | 13.0716 | 37 | 29.4617 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 7.5383 | 180 | 2.9171 | 12.6848 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0728 | 474.5809 | 1141.6808 |  | 667.0999 | 10809.2763 | 3056.2414 | 1110.7588 | 0.21947 | 18.0172 | 25.4262 | 0.02 | 0.05 | 30 | 165 | 453 | 676.8837 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 616.3388 | 30.5123 | 1.1253 | 1.0213 | 194.0999 | 473 | 438 | 442.4877 | 234.3961 | 0.2189 | 0.027 | 1.06 | 11.6354 | 11.6354 | 676.8837 | 667.0999 | 1.1253 | 1.1227 | 2.9042 | 2.7799 | 676.8837 | 667.0999 | 12.8002 | 1.1253 | 1.1227 | 298.15 | 1.9342 | 1.8514 | 676.8837 | 6.4193 | 1.1253 | 298.15 | 0.96999 | 0.9285 | 3.0562 | 3.9454 | 25.4262 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.095777 | 0.095777 | 12.8002 | 435 | 442.4877 | 1.0628 | 1.0651 | 298.15 | 0.32954 | 0.36296 | 1.0393 | 453 | 2816.5993 | 6.5855 | 0.8915 | 1.0439 | 21.47 | 123.3849 | 0.4174 | 0.076999 | 0.076999 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 85.7618 | 42.582 | 0.14818 | 0.26191 | 0.68805 | 85.7618 | 54.7906 | 0.18885 | 0.26881 | 0.70617 | 5.675 | 4.91 | 0.80891 | 0.54031 | 0.89393 | 1.0576 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 52.2042 | 0.18794 | 40.8926 | 0.14721 | 8.955 | 0.032238 | 0.11335 | 9.8837 | 0.035581 | 0.12511 | 0.08176 | 0.070739 | 294.3352 | 254.6606 | 0.0077616 | 0.0051843 | 27.9416 | 18.6635 | 0.017297 | 0.01593 | 62.2688 | 57.3495 | 8.7312 | 8.8555 | 3.0562 | 3.7226 | 1.5712 | 1.4885 | 0.79572 | 0.94816 | 0.8915 | 1.0439 | 0.26191 | 0.68805 | 19.2195 | 3056.2414 | 3945.4234 | 1.0393 | 1.217 | 85.7618 | 225.2965 | 0.27843 | 0.35943 | 0.25432 | 0.29781 | 0.60577 | 0.60482 | 0.26267 | 0.33909 | 0.49589 | 0.637 | 0.65909 | 0.29379 | 0.14721 | 0.12511 | 384.5456 | 330.6736
2013-01-10 | 6 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 26833.1196 | 19 | 73898.5433 | 17 | 2 | 5 | 402.2111 | 79.5638 | 180 | 3.2086 | 17 | 1250 | 81585.8314 | 9716.316 | 304.3183 | 10.9552 | 14.0245 | 37 | 29.243 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 7.757 | 180 | 3.0692 | 12.6858 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0732 | 475.8802 | 1144.8065 |  | 668.9263 | 10839.6823 | 3079.106 | 1118.0467 | 0.22091 | 17.9011 | 22.1011 | 0.02 | 0.05 | 30 | 165 | 453 | 675.2111 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 528.545 | 26.1641 | 1.1249 | 1.0203 | 195.9263 | 473 | 438 | 446.8359 | 228.3751 | 0.2189 | 0.027 | 1.06 | 11.7117 | 11.7117 | 675.2111 | 668.9263 | 1.1249 | 1.1232 | 2.883 | 2.8032 | 675.2111 | 668.9263 | 12.8011 | 1.1249 | 1.1232 | 298.15 | 1.9201 | 1.8669 | 675.2111 | 6.4198 | 1.1249 | 298.15 | 0.96292 | 0.93626 | 3.0791 | 3.9758 | 22.1011 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.083252 | 0.083252 | 12.8011 | 435 | 446.8359 | 1.0625 | 1.0661 | 298.15 | 0.32946 | 0.3829 | 0.89127 | 453 | 2816.5993 | 6.5855 | 0.76451 | 1.0534 | 21.47 | 122.4695 | 0.41435 | 0.07687 | 0.07687 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 85.2091 | 45.9334 | 0.15934 | 0.26211 | 0.66143 | 85.2091 | 58.7784 | 0.20214 | 0.26932 | 0.67963 | 5.7496 | 4.9327 | 0.90936 | 0.51386 | 0.76713 | 1.067 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 52.2728 | 0.18818 | 40.7722 | 0.14678 | 8.9976 | 0.032391 | 0.11389 | 9.9122 | 0.035684 | 0.12547 | 0.082835 | 0.071066 | 298.2062 | 255.837 | 0.0087253 | 0.0049305 | 31.4112 | 17.7498 | 0.017186 | 0.015661 | 61.8689 | 56.3793 | 8.8287 | 8.9086 | 3.0791 | 3.8327 | 1.5372 | 1.484 | 0.68126 | 0.97017 | 0.76451 | 1.0534 | 0.26211 | 0.66143 | 19.2209 | 3079.106 | 3975.8294 | 0.89127 | 1.2281 | 85.2091 | 215.0261 | 0.27868 | 0.35984 | 0.21667 | 0.29855 | 0.6206 | 0.62651 | 0.26291 | 0.33947 | 0.4283 | 0.65374 | 0.62789 | 0.34284 | 0.14678 | 0.12547 | 391.4862 | 329.9661
2013-01-11 | 7 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 27531.029 | 19 | 74469.0322 | 17 | 2 | 5 | 409.1781 | 82.8307 | 180 | 3.3314 | 17 | 1250 | 81839.1541 | 9928.8215 | 298.9651 | 10.6445 | 13.8189 | 37 | 29.4483 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 7.5517 | 180 | 3.1743 | 12.6896 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0744 | 481.0627 | 1157.2739 |  | 676.2112 | 10961.006 | 3102.8763 | 1147.1262 | 0.22665 | 17.5862 | 23.0085 | 0.02 | 0.05 | 30 | 165 | 453 | 682.1781 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 548.7695 | 27.1571 | 1.1267 | 1.0217 | 203.2112 | 473 | 438 | 445.8429 | 236.3352 | 0.2189 | 0.027 | 1.06 | 12.0164 | 12.0164 | 682.1781 | 676.2112 | 1.1267 | 1.1251 | 2.9733 | 2.8966 | 682.1781 | 676.2112 | 12.8049 | 1.1267 | 1.1251 | 298.15 | 1.9802 | 1.9292 | 682.1781 | 6.4217 | 1.1267 | 298.15 | 0.99308 | 0.96748 | 3.1029 | 4.0972 | 23.0085 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.08667 | 0.08667 | 12.8049 | 435 | 445.8429 | 1.0625 | 1.0659 | 298.15 | 0.32959 | 0.37843 | 0.92538 | 453 | 2816.5993 | 6.5855 | 0.79376 | 1.0947 | 21.47 | 123.3291 | 0.41722 | 0.076991 | 0.076991 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 83.7102 | 44.633 | 0.15501 | 0.25678 | 0.67333 | 83.7102 | 57.918 | 0.19927 | 0.26411 | 0.69255 | 5.9402 | 5.0226 | 0.94353 | 0.54267 | 0.79662 | 1.1095 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 52.8675 | 0.19032 | 40.3074 | 0.14511 | 9.1547 | 0.032957 | 0.11588 | 10.1303 | 0.036469 | 0.12823 | 0.08558 | 0.07236 | 308.0892 | 260.4964 | 0.0090533 | 0.005207 | 32.5918 | 18.7451 | 0.017843 | 0.016376 | 64.2353 | 58.9548 | 9.0431 | 9.1197 | 3.1029 | 3.9612 | 1.6018 | 1.5507 | 0.70709 | 1.0081 | 0.79376 | 1.0947 | 0.25678 | 0.67333 | 19.2267 | 3102.8763 | 4097.1531 | 0.92538 | 1.2763 | 83.7102 | 219.5066 | 0.27371 | 0.36142 | 0.21927 | 0.30241 | 0.63221 | 0.69476 | 0.25822 | 0.34096 | 0.42838 | 0.65006 | 0.61506 | 0.3235 | 0.14511 | 0.12823 | 404.9163 | 338.1962
2013-01-13 | 8 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 27966.3507 | 19 | 78690.2667 | 17 | 2 | 5 | 373.7094 | 76.8385 | 180 | 3.1122 | 17 | 1250 | 45135.3389 | 4891.7404 | 139.0278 | 14.9956 | 17.5347 | 37 | 29.1429 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 7.8571 | 180 | 2.5391 | 12.692 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0752 | 484.2937 | 1165.0466 |  | 680.7529 | 11036.6817 | 3278.7611 | 1165.2646 | 0.23024 | 8.1781 | 21.344 | 0.02 | 0.05 | 30 | 165 | 453 | 646.7094 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 512.6696 | 25.3659 | 1.1172 | 1.0153 | 207.7529 | 473 | 438 | 447.6341 | 199.0753 | 0.2189 | 0.027 | 1.06 | 12.2064 | 12.2064 | 646.7094 | 680.7529 | 1.1172 | 1.1263 | 2.5287 | 2.9555 | 646.7094 | 680.7529 | 12.8073 | 1.1172 | 1.1263 | 298.15 | 1.6841 | 1.9683 | 646.7094 | 6.4229 | 1.1172 | 298.15 | 0.8446 | 0.98713 | 3.2788 | 4.1728 | 21.344 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.0804 | 0.0804 | 12.8073 | 435 | 447.6341 | 1.0624 | 1.0663 | 298.15 | 0.32961 | 0.38678 | 0.8645 | 453 | 2816.5993 | 6.5855 | 0.74155 | 1.11 | 21.47 | 122.0506 | 0.41296 | 0.076811 | 0.076811 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 38.9278 | 62.8426 | 0.21568 | 0.12408 | 0.88149 | 38.9278 | 73.4689 | 0.25109 | 0.12681 | 0.90085 | 6.3989 | 5.0781 | 0.69338 | 0.552 | 0.73962 | 1.1247 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 52.8198 | 0.19015 | 40.0293 | 0.14411 | 7.4148 | 0.026693 | 0.093859 | 10.4048 | 0.037457 | 0.13171 | 0.092189 | 0.07316 | 331.8788 | 263.3748 | 0.006653 | 0.0052965 | 23.9509 | 19.0673 | 0.014539 | 0.016577 | 52.3419 | 59.6774 | 9.6776 | 9.2509 | 3.2788 | 4.9487 | 1.2974 | 1.5816 | 0.66115 | 1.0296 | 0.74155 | 1.11 | 0.12408 | 0.88149 | 19.2302 | 3278.7611 | 4172.8289 | 0.8645 | 1.294 | 38.9278 | 276.5483 | 0.28473 | 0.36237 | 0.20167 | 0.30186 | 0.56477 | 0.4566 | 0.26861 | 0.34186 | 0.4881 | 0.65098 | 0.79416 | 0.16733 | 0.14411 | 0.13171 | 408.1716 | 342.1195
2013-01-14 | 9 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 31161.2827 | 19 | 78486.9933 | 17 | 2 | 5 | 410.6665 | 84.8012 | 180 | 3.3033 | 17 | 1250 | 85995.4818 | 9762.0578 | 279.113 | 12.2758 | 15.8408 | 37 | 29.2937 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 7.7063 | 180 | 3.565 | 12.7093 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0811 | 507.9702 | 1222.0043 |  | 714.034 | 11592.0846 | 3270.2914 | 1298.3868 | 0.25654 | 16.4184 | 23.5559 | 0.02 | 0.05 | 30 | 165 | 453 | 683.6665 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 544.1504 | 26.8867 | 1.1271 | 1.0219 | 241.034 | 473 | 438 | 446.1133 | 237.5532 | 0.2189 | 0.027 | 1.06 | 13.6008 | 13.6008 | 683.6665 | 714.034 | 1.1271 | 1.1353 | 2.9972 | 3.3996 | 683.6665 | 714.034 | 12.8249 | 1.1271 | 1.1353 | 298.15 | 1.9961 | 2.2641 | 683.6665 | 6.4317 | 1.1271 | 298.15 | 1.0011 | 1.1355 | 3.2703 | 4.7282 | 23.5559 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.088732 | 0.088732 | 12.8249 | 435 | 446.1133 | 1.0625 | 1.066 | 298.15 | 0.33009 | 0.38026 | 0.91759 | 453 | 2816.5993 | 6.5855 | 0.78708 | 1.301 | 21.47 | 122.6816 | 0.41506 | 0.0769 | 0.0769 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 78.1517 | 51.46 | 0.17776 | 0.24324 | 0.74671 | 78.1517 | 66.38 | 0.22747 | 0.25093 | 0.7703 | 7.3334 | 5.473 | 0.96768 | 0.67161 | 0.7902 | 1.32 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 57.0361 | 0.20533 | 38.223 | 0.1376 | 9.974 | 0.035906 | 0.12625 | 11.2748 | 0.040589 | 0.14272 | 0.10565 | 0.07885 | 380.347 | 283.8601 | 0.0092849 | 0.0064441 | 33.4257 | 23.1989 | 0.018088 | 0.019682 | 65.1175 | 70.8567 | 10.6037 | 10.2013 | 3.2703 | 5.4212 | 1.6159 | 1.8839 | 0.69835 | 1.2122 | 0.78708 | 1.301 | 0.24324 | 0.74671 | 19.2565 | 3270.2914 | 4728.2318 | 0.91759 | 1.5167 | 78.1517 | 239.9099 | 0.25487 | 0.3685 | 0.19213 | 0.31758 | 0.59155 | 0.82399 | 0.24045 | 0.34764 | 0.41917 | 0.64349 | 0.57396 | 0.30905 | 0.1376 | 0.14272 | 478.8902 | 377.9157
2013-01-15 | 10 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 27920.7102 | 19 | 78284.2589 | 17 | 2 | 5 | 403.4981 | 80.8841 | 180 | 3.2403 | 17 | 1250 | 92029.2989 | 10074.7349 | 320.2663 | 11.0827 | 14.3478 | 37 | 29.4379 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 7.5621 | 180 | 3.2651 | 12.6917 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0751 | 483.955 | 1164.2318 |  | 680.2768 | 11028.7477 | 3261.8441 | 1163.3629 | 0.22986 | 18.8392 | 22.4678 | 0.02 | 0.05 | 30 | 165 | 453 | 676.4981 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 533.7683 | 26.4103 | 1.1252 | 1.0206 | 207.2768 | 473 | 438 | 446.5897 | 229.9085 | 0.2189 | 0.027 | 1.06 | 12.1864 | 12.1864 | 676.4981 | 680.2768 | 1.1252 | 1.1262 | 2.9008 | 2.9493 | 676.4981 | 680.2768 | 12.8071 | 1.1252 | 1.1262 | 298.15 | 1.9319 | 1.9642 | 676.4981 | 6.4228 | 1.1252 | 298.15 | 0.96887 | 0.98506 | 3.2618 | 4.1649 | 22.4678 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.084633 | 0.084633 | 12.8071 | 435 | 446.5897 | 1.0625 | 1.0661 | 298.15 | 0.32962 | 0.38194 | 0.90008 | 453 | 2816.5993 | 6.5855 | 0.77207 | 1.1153 | 21.47 | 123.2853 | 0.41707 | 0.076985 | 0.076985 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 89.6746 | 46.4668 | 0.16112 | 0.27616 | 0.67221 | 89.6746 | 60.1316 | 0.20665 | 0.28423 | 0.69186 | 6.0238 | 5.0723 | 0.91487 | 0.55161 | 0.77566 | 1.1305 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 51.3624 | 0.1849 | 40.058 | 0.14421 | 9.3564 | 0.033683 | 0.11844 | 10.245 | 0.036882 | 0.12968 | 0.086785 | 0.073076 | 312.4258 | 263.074 | 0.0087783 | 0.0052927 | 31.6018 | 19.0538 | 0.017347 | 0.016652 | 62.4509 | 59.9485 | 9.2856 | 9.2372 | 3.2618 | 4.251 | 1.55 | 1.5823 | 0.68743 | 1.0307 | 0.77207 | 1.1153 | 0.27616 | 0.67221 | 19.2299 | 3261.8441 | 4164.8948 | 0.90008 | 1.3002 | 89.6746 | 218.2812 | 0.28372 | 0.36227 | 0.21031 | 0.3038 | 0.57047 | 0.72793 | 0.26766 | 0.34176 | 0.42903 | 0.65138 | 0.60271 | 0.35769 | 0.14421 | 0.12968 | 406.4785 | 342.0764
2013-01-16 | 11 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 28257.6749 | 19 | 79704.4494 | 17 | 2 | 5 | 400.0546 | 78.5103 | 180 | 3.1114 | 17 | 1250 | 89326.0852 | 10583.8519 | 292.5282 | 11.3346 | 14.9101 | 37 | 29.6149 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 7.3851 | 180 | 3.5755 | 12.6935 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0758 | 486.4553 | 1170.2467 |  | 683.7914 | 11087.3252 | 3321.0187 | 1177.4031 | 0.23263 | 17.2075 | 21.8084 | 0.02 | 0.05 | 30 | 165 | 453 | 673.0546 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 512.5446 | 25.3565 | 1.1243 | 1.0198 | 210.7914 | 473 | 438 | 447.6435 | 225.4111 | 0.2189 | 0.027 | 1.06 | 12.3335 | 12.3335 | 673.0546 | 683.7914 | 1.1243 | 1.1272 | 2.8573 | 2.9951 | 673.0546 | 683.7914 | 12.8089 | 1.1243 | 1.1272 | 298.15 | 1.9029 | 1.9947 | 673.0546 | 6.4237 | 1.1243 | 298.15 | 0.95433 | 1.0004 | 3.321 | 4.2235 | 21.8084 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.08215 | 0.08215 | 12.8089 | 435 | 447.6435 | 1.0624 | 1.0663 | 298.15 | 0.32965 | 0.38688 | 0.86429 | 453 | 2816.5993 | 6.5855 | 0.74137 | 1.1335 | 21.47 | 124.0263 | 0.41954 | 0.07709 | 0.07709 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 81.9079 | 47.5211 | 0.16463 | 0.25281 | 0.6308 | 81.9079 | 62.485 | 0.21449 | 0.26089 | 0.65096 | 6.1552 | 5.115 | 0.91408 | 0.55654 | 0.74507 | 1.1492 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 51.274 | 0.18459 | 39.8479 | 0.14345 | 9.2961 | 0.033466 | 0.11767 | 10.3044 | 0.037096 | 0.13044 | 0.088678 | 0.073691 | 319.2423 | 265.2891 | 0.0087706 | 0.00534 | 31.5742 | 19.2241 | 0.017062 | 0.016864 | 61.4227 | 60.7117 | 9.4762 | 9.3384 | 3.321 | 4.4682 | 1.5161 | 1.6078 | 0.65922 | 1.0513 | 0.74137 | 1.1335 | 0.25281 | 0.6308 | 19.2326 | 3321.0187 | 4223.4723 | 0.86429 | 1.3214 | 81.9079 | 204.3747 | 0.28542 | 0.36298 | 0.19954 | 0.30507 | 0.61743 | 0.90006 | 0.26927 | 0.34244 | 0.419 | 0.65386 | 0.55653 | 0.34101 | 0.14345 | 0.13044 | 412.2391 | 345.225
2013-01-17 | 12 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 27991.9369 | 19 | 79189.9583 | 17 | 2 | 5 | 399.1233 | 80.9992 | 180 | 3.2244 | 17 | 1250 | 90489.2439 | 10818.3546 | 312.4951 | 11.1615 | 14.5551 | 37 | 29.0322 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 7.9678 | 180 | 3.3937 | 12.6921 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0753 | 484.4836 | 1165.5034 |  | 681.0198 | 11041.1296 | 3299.5816 | 1166.3307 | 0.23045 | 18.3821 | 22.4998 | 0.02 | 0.05 | 30 | 165 | 453 | 672.1233 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 531.1444 | 26.2797 | 1.124 | 1.0198 | 208.0198 | 473 | 438 | 446.7203 | 225.403 | 0.2189 | 0.027 | 1.06 | 12.2175 | 12.2175 | 672.1233 | 681.0198 | 1.124 | 1.1264 | 2.8451 | 2.9589 | 672.1233 | 681.0198 | 12.8075 | 1.124 | 1.1264 | 298.15 | 1.8948 | 1.9707 | 672.1233 | 6.423 | 1.124 | 298.15 | 0.95026 | 0.98829 | 3.2996 | 4.1773 | 22.4998 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.084754 | 0.084754 | 12.8075 | 435 | 446.7203 | 1.0625 | 1.0661 | 298.15 | 0.32963 | 0.38255 | 0.89566 | 453 | 2816.5993 | 6.5855 | 0.76827 | 1.1182 | 21.47 | 121.5874 | 0.41142 | 0.076745 | 0.076745 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 87.4986 | 46.7965 | 0.16222 | 0.26965 | 0.64133 | 87.4986 | 60.9994 | 0.20954 | 0.27784 | 0.66081 | 6.0728 | 5.0813 | 0.88169 | 0.55469 | 0.77174 | 1.1329 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 51.1539 | 0.18415 | 40.0132 | 0.14405 | 9.3309 | 0.033591 | 0.11811 | 10.2365 | 0.036851 | 0.12958 | 0.087492 | 0.073206 | 314.9695 | 263.5433 | 0.0084599 | 0.0053222 | 30.4555 | 19.1601 | 0.016957 | 0.016705 | 61.0442 | 60.139 | 9.3724 | 9.2586 | 3.2996 | 4.38 | 1.5123 | 1.5881 | 0.68352 | 1.0334 | 0.76827 | 1.1182 | 0.26965 | 0.64133 | 19.2304 | 3299.5816 | 4177.2768 | 0.89566 | 1.3036 | 87.4986 | 208.1072 | 0.28627 | 0.36242 | 0.20874 | 0.30381 | 0.623 | 0.70908 | 0.27007 | 0.34191 | 0.43669 | 0.65073 | 0.57355 | 0.35098 | 0.14405 | 0.12958 | 406.4693 | 342.8423
2013-01-18 | 13 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 27838.2344 | 19 | 76807.3792 | 17 | 2 | 5 | 403.5732 | 85.3194 | 180 | 3.3986 | 17 | 1250 | 78457.8676 | 9291.462 | 285.302 | 11.1044 | 14.0343 | 37 | 28.2415 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 8.7585 | 180 | 2.9299 | 12.6913 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.075 | 483.3429 | 1162.7594 |  | 679.4164 | 11014.4102 | 3200.3075 | 1159.9264 | 0.22918 | 16.7825 | 23.6998 | 0.02 | 0.05 | 30 | 165 | 453 | 676.5732 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 559.8391 | 27.7013 | 1.1252 | 1.0208 | 206.4164 | 473 | 438 | 445.2987 | 231.2745 | 0.2189 | 0.027 | 1.06 | 12.1504 | 12.1504 | 676.5732 | 679.4164 | 1.1252 | 1.126 | 2.9017 | 2.9381 | 676.5732 | 679.4164 | 12.8066 | 1.1252 | 1.126 | 298.15 | 1.9325 | 1.9568 | 676.5732 | 6.4225 | 1.1252 | 298.15 | 0.96915 | 0.98133 | 3.2003 | 4.1506 | 23.6998 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.089274 | 0.089274 | 12.8066 | 435 | 445.2987 | 1.0626 | 1.0658 | 298.15 | 0.32964 | 0.37597 | 0.94404 | 453 | 2816.5993 | 6.5855 | 0.80978 | 1.1107 | 21.47 | 118.2782 | 0.40039 | 0.076277 | 0.076277 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 79.8846 | 46.5577 | 0.16142 | 0.24606 | 0.71843 | 79.8846 | 58.8195 | 0.20228 | 0.25251 | 0.73727 | 6.0485 | 5.0618 | 0.88236 | 0.55942 | 0.81104 | 1.1243 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 52.1841 | 0.18786 | 40.1102 | 0.1444 | 9.152 | 0.032947 | 0.11585 | 10.26 | 0.036936 | 0.12987 | 0.087141 | 0.072925 | 313.7059 | 262.5299 | 0.0084663 | 0.0053677 | 30.4786 | 19.3238 | 0.017312 | 0.016697 | 62.324 | 60.1077 | 9.2488 | 9.2123 | 3.2003 | 4.2153 | 1.5565 | 1.5808 | 0.7205 | 1.0214 | 0.80978 | 1.1107 | 0.24606 | 0.71843 | 19.2292 | 3200.3075 | 4150.5573 | 0.94404 | 1.2948 | 79.8846 | 233.244 | 0.27919 | 0.36209 | 0.22123 | 0.30343 | 0.61712 | 0.47821 | 0.26339 | 0.3416 | 0.44951 | 0.64612 | 0.64685 | 0.30386 | 0.1444 | 0.12987 | 406.5085 | 341.9614
2013-01-23 | 14 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 28225.9995 | 19 | 76888.3347 | 17 | 2 | 5 | 402.7138 | 78.6819 | 180 | 3.1315 | 17 | 1250 | 89425.6327 | 8774.117 | 261.7313 | 10.8548 | 14.1707 | 37 | 28.8957 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 8.1043 | 180 | 3.3159 | 12.6934 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0757 | 486.2203 | 1169.6813 |  | 683.461 | 11081.8188 | 3203.6806 | 1176.0833 | 0.23237 | 15.396 | 21.8561 | 0.02 | 0.05 | 30 | 165 | 453 | 675.7138 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 515.8459 | 25.5202 | 1.125 | 1.0203 | 210.461 | 473 | 438 | 447.4798 | 228.234 | 0.2189 | 0.027 | 1.06 | 12.3197 | 12.3197 | 675.7138 | 683.461 | 1.125 | 1.1271 | 2.8911 | 2.9908 | 675.7138 | 683.461 | 12.8088 | 1.125 | 1.1271 | 298.15 | 1.9255 | 1.9918 | 675.7138 | 6.4236 | 1.125 | 298.15 | 0.96564 | 0.99891 | 3.2037 | 4.218 | 21.8561 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.082329 | 0.082329 | 12.8088 | 435 | 447.4798 | 1.0624 | 1.0663 | 298.15 | 0.32965 | 0.38611 | 0.86986 | 453 | 2816.5993 | 6.5855 | 0.74614 | 1.1324 | 21.47 | 121.0162 | 0.40951 | 0.076664 | 0.076664 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 73.2848 | 45.513 | 0.15794 | 0.22522 | 0.66218 | 73.2848 | 59.3906 | 0.20418 | 0.23193 | 0.68188 | 6.2249 | 5.111 | 0.93204 | 0.55568 | 0.74804 | 1.1473 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 52.9375 | 0.19057 | 39.8675 | 0.14352 | 9.0893 | 0.032721 | 0.11505 | 10.3263 | 0.037175 | 0.13071 | 0.089682 | 0.073634 | 322.854 | 265.0815 | 0.008943 | 0.0053318 | 32.1948 | 19.1945 | 0.017255 | 0.016834 | 62.1192 | 60.6016 | 9.4285 | 9.3289 | 3.2037 | 4.3945 | 1.5394 | 1.6057 | 0.66381 | 1.0501 | 0.74614 | 1.1324 | 0.22522 | 0.66218 | 19.2324 | 3203.6806 | 4217.9659 | 0.86986 | 1.3201 | 73.2848 | 215.4622 | 0.27565 | 0.36292 | 0.20105 | 0.30512 | 0.51129 | 0.66132 | 0.26005 | 0.34238 | 0.41596 | 0.65394 | 0.58476 | 0.30185 | 0.14352 | 0.13071 | 417.168 | 344.8775
2013-01-25 | 15 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 25929.7009 | 19 | 69939.1892 | 17 | 2 | 5 | 398.7097 | 79.989 | 180 | 3.1134 | 17 | 1250 | 79553.0144 | 8766.3667 | 268.723 | 12.5136 | 15.6287 | 37 | 29.014 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 7.986 | 180 | 3.1151 | 12.6809 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0715 | 469.167 | 1128.6569 |  | 659.4899 | 10682.6332 | 2914.1329 | 1080.4042 | 0.21347 | 15.8072 | 22.2192 | 0.02 | 0.05 | 30 | 165 | 453 | 671.7097 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 512.8701 | 25.398 | 1.1239 | 1.0195 | 186.4899 | 473 | 438 | 447.602 | 224.1076 | 0.2189 | 0.027 | 1.06 | 11.3174 | 11.3174 | 671.7097 | 659.4899 | 1.1239 | 1.1206 | 2.8373 | 2.6838 | 671.7097 | 659.4899 | 12.7962 | 1.1239 | 1.1206 | 298.15 | 1.8897 | 1.7874 | 671.7097 | 6.4173 | 1.1239 | 298.15 | 0.94767 | 0.89639 | 2.9141 | 3.8188 | 22.2192 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.083697 | 0.083697 | 12.7962 | 435 | 447.602 | 1.0624 | 1.0663 | 298.15 | 0.32932 | 0.3863 | 0.86484 | 453 | 2816.5993 | 6.5855 | 0.74184 | 1.0015 | 21.47 | 121.5113 | 0.41116 | 0.076734 | 0.076734 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 75.2424 | 52.4553 | 0.18107 | 0.23468 | 0.61505 | 75.2424 | 65.4924 | 0.22451 | 0.24115 | 0.63199 | 5.566 | 4.8148 | 0.90221 | 0.48336 | 0.74357 | 1.0137 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 53.5084 | 0.19263 | 41.4117 | 0.14908 | 8.5899 | 0.030924 | 0.10873 | 9.5995 | 0.034558 | 0.12151 | 0.080189 | 0.069367 | 288.6798 | 249.7228 | 0.0086567 | 0.0046379 | 31.1643 | 16.6963 | 0.016915 | 0.014849 | 60.8943 | 53.4555 | 8.4801 | 8.6336 | 2.9141 | 3.5405 | 1.5034 | 1.4011 | 0.65814 | 0.91776 | 0.74184 | 1.0015 | 0.23468 | 0.61505 | 19.2135 | 2914.1329 | 3818.7803 | 0.86484 | 1.1675 | 75.2424 | 197.1928 | 0.27294 | 0.35767 | 0.21756 | 0.2937 | 0.57423 | 0.61117 | 0.25749 | 0.33742 | 0.42179 | 0.65502 | 0.61415 | 0.31635 | 0.14908 | 0.12151 | 380.7383 | 319.8745
2013-01-29 | 17 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 27485.6641 | 19 | 78350.5869 | 17 | 2 | 5 | 399.5737 | 79.9503 | 180 | 3.0568 | 17 | 1250 | 79552.5643 | 9600.797 | 284.7679 | 12.493 | 15.7361 | 37 | 29.7149 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 7.2851 | 180 | 3.2431 | 12.6893 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0743 | 480.7259 | 1156.4637 |  | 675.7378 | 10953.1198 | 3264.6078 | 1145.236 | 0.22628 | 16.7511 | 22.2084 | 0.02 | 0.05 | 30 | 165 | 453 | 672.5737 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 503.5405 | 24.9193 | 1.1241 | 1.0196 | 202.7378 | 473 | 438 | 448.0807 | 224.4931 | 0.2189 | 0.027 | 1.06 | 11.9966 | 11.9966 | 672.5737 | 675.7378 | 1.1241 | 1.125 | 2.8502 | 2.8905 | 672.5737 | 675.7378 | 12.8047 | 1.1241 | 1.125 | 298.15 | 1.8982 | 1.9251 | 672.5737 | 6.4216 | 1.1241 | 298.15 | 0.95197 | 0.96544 | 3.2646 | 4.0893 | 22.2084 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.083656 | 0.083656 | 12.8047 | 435 | 448.0807 | 1.0624 | 1.0664 | 298.15 | 0.32953 | 0.38878 | 0.84911 | 453 | 2816.5993 | 6.5855 | 0.72834 | 1.0897 | 21.47 | 124.4446 | 0.42094 | 0.077149 | 0.077149 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 79.735 | 52.3691 | 0.18079 | 0.24865 | 0.67168 | 79.735 | 65.9418 | 0.22601 | 0.25578 | 0.69095 | 5.8817 | 5.0168 | 0.92402 | 0.53031 | 0.73116 | 1.1046 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 50.7042 | 0.18253 | 40.3369 | 0.14521 | 9.0739 | 0.032666 | 0.11486 | 10.1153 | 0.036415 | 0.12804 | 0.084738 | 0.072276 | 305.0578 | 260.1952 | 0.0088661 | 0.0050883 | 31.9178 | 18.318 | 0.017071 | 0.016186 | 61.455 | 58.2692 | 9.1464 | 9.106 | 3.2646 | 4.1614 | 1.5095 | 1.5363 | 0.64469 | 1.006 | 0.72834 | 1.0897 | 0.24865 | 0.67168 | 19.2263 | 3264.6078 | 4089.2669 | 0.84911 | 1.2703 | 79.735 | 215.3898 | 0.28846 | 0.36132 | 0.20153 | 0.30151 | 0.62889 | 0.76988 | 0.27213 | 0.34087 | 0.41097 | 0.65482 | 0.61641 | 0.34139 | 0.14521 | 0.12804 | 398.4307 | 336.7825
2013-01-30 | 18 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 27477.4267 | 19 | 79398.5419 | 17 | 2 | 5 | 400.8171 | 81.4993 | 180 | 3.2183 | 17 | 1250 | 81364.982 | 10010.0696 | 327.3393 | 11.0516 | 13.9998 | 37 | 28.7763 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 8.2237 | 180 | 2.9483 | 12.6893 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0743 | 480.6648 | 1156.3166 |  | 675.6518 | 10951.6878 | 3308.2726 | 1144.8928 | 0.22621 | 19.2553 | 22.6387 | 0.02 | 0.05 | 30 | 165 | 453 | 673.8171 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 530.144 | 26.236 | 1.1245 | 1.0201 | 202.6518 | 473 | 438 | 446.764 | 227.0531 | 0.2189 | 0.027 | 1.06 | 11.993 | 11.993 | 673.8171 | 675.6518 | 1.1245 | 1.125 | 2.866 | 2.8894 | 673.8171 | 675.6518 | 12.8047 | 1.1245 | 1.125 | 298.15 | 1.9088 | 1.9244 | 673.8171 | 6.4216 | 1.1245 | 298.15 | 0.95725 | 0.96507 | 3.3083 | 4.0878 | 22.6387 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.085277 | 0.085277 | 12.8047 | 435 | 446.764 | 1.0625 | 1.0661 | 298.15 | 0.32956 | 0.38267 | 0.89397 | 453 | 2816.5993 | 6.5855 | 0.76682 | 1.0895 | 21.47 | 120.5164 | 0.40785 | 0.076593 | 0.076593 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 91.655 | 46.3365 | 0.16069 | 0.28218 | 0.70828 | 91.655 | 58.6753 | 0.2018 | 0.28963 | 0.72698 | 5.8187 | 5.0157 | 0.89767 | 0.53745 | 0.76941 | 1.1034 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 49.9504 | 0.17982 | 40.3422 | 0.14523 | 9.2698 | 0.033371 | 0.11734 | 10.1443 | 0.036519 | 0.12841 | 0.08383 | 0.072261 | 301.7866 | 260.1405 | 0.0086132 | 0.0051568 | 31.0074 | 18.5646 | 0.017106 | 0.016253 | 61.5816 | 58.5091 | 9.1269 | 9.1035 | 3.3083 | 4.1296 | 1.5261 | 1.5417 | 0.68155 | 1.0042 | 0.76682 | 1.0895 | 0.28218 | 0.70828 | 19.2262 | 3308.2726 | 4087.835 | 0.89397 | 1.2702 | 91.655 | 230.0563 | 0.2924 | 0.3613 | 0.21224 | 0.30156 | 0.6411 | 0.53333 | 0.27585 | 0.34085 | 0.43157 | 0.65139 | 0.65008 | 0.36798 | 0.14523 | 0.12841 | 394.3756 | 337.2141
2013-01-31 | 19 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 27477.8217 | 19 | 80339.9175 | 17 | 2 | 5 | 403.3537 | 82.0882 | 180 | 3.2552 | 17 | 1250 | 85115.6922 | 10565.3227 | 340.8733 | 11.0928 | 14.2596 | 37 | 29.0793 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 7.9207 | 180 | 3.1668 | 12.6893 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0743 | 480.6677 | 1156.3236 |  | 675.6559 | 10951.7565 | 3347.4966 | 1144.9092 | 0.22621 | 20.0514 | 22.8023 | 0.02 | 0.05 | 30 | 165 | 453 | 676.3537 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 536.2219 | 26.5368 | 1.1252 | 1.0206 | 202.6559 | 473 | 438 | 446.4632 | 229.8905 | 0.2189 | 0.027 | 1.06 | 11.9931 | 11.9931 | 676.3537 | 675.6559 | 1.1252 | 1.125 | 2.8984 | 2.8895 | 676.3537 | 675.6559 | 12.8047 | 1.1252 | 1.125 | 298.15 | 1.9303 | 1.9244 | 676.3537 | 6.4216 | 1.1252 | 298.15 | 0.96807 | 0.96509 | 3.3475 | 4.0879 | 22.8023 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.085893 | 0.085893 | 12.8047 | 435 | 446.4632 | 1.0625 | 1.066 | 298.15 | 0.32956 | 0.38128 | 0.90422 | 453 | 2816.5993 | 6.5855 | 0.77561 | 1.0902 | 21.47 | 121.7844 | 0.41207 | 0.076773 | 0.076773 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 95.4445 | 46.5091 | 0.16126 | 0.29395 | 0.6665 | 95.4445 | 59.7624 | 0.20542 | 0.30229 | 0.6854 | 5.7472 | 5.0158 | 0.91105 | 0.53881 | 0.77926 | 1.1044 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 49.2265 | 0.17722 | 40.342 | 0.14523 | 9.332 | 0.033595 | 0.11813 | 10.1082 | 0.03639 | 0.12795 | 0.082801 | 0.072262 | 298.0819 | 260.1431 | 0.0087416 | 0.0051699 | 31.4696 | 18.6115 | 0.017353 | 0.016282 | 62.4723 | 58.6154 | 9.0947 | 9.1037 | 3.3475 | 4.072 | 1.5491 | 1.5431 | 0.68972 | 1.0043 | 0.77561 | 1.0902 | 0.29395 | 0.6665 | 19.2262 | 3347.4966 | 4087.9036 | 0.90422 | 1.271 | 95.4445 | 216.407 | 0.29586 | 0.3613 | 0.21467 | 0.30174 | 0.64684 | 0.63681 | 0.27912 | 0.34085 | 0.43087 | 0.65083 | 0.61135 | 0.379 | 0.14523 | 0.12795 | 392.0238 | 337.37
2013-02-01 | 20 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 28283.039 | 19 | 82197.8311 | 17 | 2 | 5 | 402.7289 | 84.1766 | 180 | 3.2979 | 17 | 1250 | 86215.2134 | 10928.7481 | 333.4152 | 11.9327 | 15.2018 | 37 | 29.4088 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 7.5912 | 180 | 3.2691 | 12.6937 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0758 | 486.6435 | 1170.6993 |  | 684.0559 | 11091.7344 | 3424.9096 | 1178.46 | 0.23284 | 19.6127 | 23.3824 | 0.02 | 0.05 | 30 | 165 | 453 | 675.7289 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 543.2599 | 26.8758 | 1.125 | 1.0205 | 211.0559 | 473 | 438 | 446.1242 | 229.6047 | 0.2189 | 0.027 | 1.06 | 12.3446 | 12.3446 | 675.7289 | 684.0559 | 1.125 | 1.1272 | 2.8914 | 2.9985 | 675.7289 | 684.0559 | 12.8091 | 1.125 | 1.1272 | 298.15 | 1.9257 | 1.997 | 675.7289 | 6.4238 | 1.125 | 298.15 | 0.96573 | 1.0015 | 3.4249 | 4.2279 | 23.3824 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.088079 | 0.088079 | 12.8091 | 435 | 446.1242 | 1.0625 | 1.066 | 298.15 | 0.32969 | 0.37984 | 0.91609 | 453 | 2816.5993 | 6.5855 | 0.78579 | 1.1356 | 21.47 | 123.1636 | 0.41667 | 0.076968 | 0.076968 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 93.3563 | 50.0242 | 0.17297 | 0.28968 | 0.69103 | 93.3563 | 63.7055 | 0.21856 | 0.2981 | 0.71111 | 6.0283 | 5.1182 | 0.89828 | 0.56964 | 0.78972 | 1.1512 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 49.6217 | 0.17864 | 39.8323 | 0.1434 | 9.5194 | 0.03427 | 0.1205 | 10.3696 | 0.03733 | 0.13126 | 0.086849 | 0.073738 | 312.6574 | 265.4554 | 0.008619 | 0.0054657 | 31.0285 | 19.6766 | 0.017333 | 0.017052 | 62.3984 | 61.3885 | 9.4532 | 9.3461 | 3.4249 | 4.4177 | 1.5458 | 1.6172 | 0.69772 | 1.0475 | 0.78579 | 1.1356 | 0.28968 | 0.69103 | 19.2328 | 3424.9096 | 4227.8816 | 0.91609 | 1.3239 | 93.3563 | 222.6983 | 0.29409 | 0.36304 | 0.21131 | 0.30538 | 0.66056 | 0.72446 | 0.27744 | 0.34249 | 0.43717 | 0.64776 | 0.60851 | 0.36865 | 0.1434 | 0.13126 | 406.0843 | 346.5206
2013-02-03 | 21 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 26475.3034 | 19 | 74892.3983 | 17 | 2 | 5 | 406.8215 | 94.0354 | 180 | 3.7328 | 17 | 1250 | 88504.8613 | 8686.7856 | 257.5877 | 12.4764 | 15.874 | 37 | 30.1888 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 6.8112 | 180 | 3.3976 | 12.6839 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0725 | 473.2219 | 1138.4116 |  | 665.1897 | 10777.48 | 3120.5166 | 1103.1376 | 0.21796 | 15.1522 | 26.121 | 0.02 | 0.05 | 30 | 165 | 453 | 679.8215 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 614.8977 | 30.4434 | 1.1261 | 1.0219 | 192.1897 | 473 | 438 | 442.5566 | 237.2648 | 0.2189 | 0.027 | 1.06 | 11.5556 | 11.5556 | 679.8215 | 665.1897 | 1.1261 | 1.1222 | 2.9416 | 2.7557 | 679.8215 | 665.1897 | 12.7992 | 1.1261 | 1.1222 | 298.15 | 1.9591 | 1.8353 | 679.8215 | 6.4188 | 1.1261 | 298.15 | 0.9825 | 0.9204 | 3.1205 | 3.9136 | 26.121 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.098394 | 0.098394 | 12.7992 | 435 | 442.5566 | 1.0628 | 1.0651 | 298.15 | 0.32951 | 0.36325 | 1.0369 | 453 | 2816.5993 | 6.5855 | 0.88941 | 1.0343 | 21.47 | 126.428 | 0.42754 | 0.07743 | 0.07743 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 72.1246 | 52.2995 | 0.18055 | 0.22488 | 0.61054 | 72.1246 | 66.5187 | 0.22793 | 0.23164 | 0.62888 | 5.4935 | 4.8863 | 0.83858 | 0.53613 | 0.89214 | 1.0486 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 50.5875 | 0.18212 | 41.0202 | 0.14767 | 8.6677 | 0.031204 | 0.10972 | 9.7559 | 0.035121 | 0.12349 | 0.079144 | 0.070396 | 284.9189 | 253.4266 | 0.0080462 | 0.0051442 | 28.9664 | 18.519 | 0.017635 | 0.015825 | 63.4857 | 56.9709 | 8.614 | 8.7999 | 3.1205 | 3.5804 | 1.5959 | 1.472 | 0.79102 | 0.93592 | 0.88941 | 1.0343 | 0.22488 | 0.61054 | 19.218 | 3120.5166 | 3913.6271 | 1.0369 | 1.2058 | 72.1246 | 195.811 | 0.28625 | 0.359 | 0.25547 | 0.29709 | 0.51147 | 0.95763 | 0.27004 | 0.33868 | 0.48541 | 0.6358 | 0.59028 | 0.25285 | 0.14767 | 0.12349 | 377.371 | 328.9165
2013-02-04 | 22 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 27222.1384 | 19 | 77706.4858 | 17 | 2 | 5 | 404.3799 | 91.6646 | 180 | 3.62 | 17 | 1250 | 81213.0533 | 8190.5147 | 251.7568 | 10.6901 | 13.7198 | 37 | 28.608 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 8.392 | 180 | 3.0297 | 12.6879 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0739 | 478.7693 | 1151.7568 |  | 672.9875 | 10907.3088 | 3237.7702 | 1134.2558 | 0.22411 | 14.8092 | 25.4624 | 0.02 | 0.05 | 30 | 165 | 453 | 677.3799 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 596.3178 | 29.514 | 1.1254 | 1.0213 | 199.9875 | 473 | 438 | 443.486 | 233.8939 | 0.2189 | 0.027 | 1.06 | 11.8815 | 11.8815 | 677.3799 | 672.9875 | 1.1254 | 1.1243 | 2.9112 | 2.8551 | 677.3799 | 672.9875 | 12.8033 | 1.1254 | 1.1243 | 298.15 | 1.9389 | 1.9015 | 677.3799 | 6.4209 | 1.1254 | 298.15 | 0.97235 | 0.95362 | 3.2378 | 4.0435 | 25.4624 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.095914 | 0.095914 | 12.8033 | 435 | 443.486 | 1.0627 | 1.0653 | 298.15 | 0.32959 | 0.36758 | 1.0056 | 453 | 2816.5993 | 6.5855 | 0.86254 | 1.076 | 21.47 | 119.812 | 0.4055 | 0.076494 | 0.076494 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 70.4919 | 44.8237 | 0.15565 | 0.21632 | 0.6726 | 70.4919 | 57.5034 | 0.19789 | 0.22221 | 0.69091 | 5.7326 | 4.9829 | 0.84265 | 0.55386 | 0.86346 | 1.0893 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 50.3412 | 0.18123 | 40.5101 | 0.14584 | 8.7738 | 0.031586 | 0.11106 | 10.0378 | 0.036136 | 0.12706 | 0.082589 | 0.071789 | 297.3202 | 258.441 | 0.0080853 | 0.0053144 | 29.1069 | 19.1317 | 0.017391 | 0.016359 | 62.6093 | 58.8926 | 8.9703 | 9.0264 | 3.2378 | 3.9434 | 1.5713 | 1.5339 | 0.76663 | 0.98008 | 0.86254 | 1.076 | 0.21632 | 0.6726 | 19.2241 | 3237.7702 | 4043.456 | 1.0056 | 1.2544 | 70.4919 | 219.1765 | 0.28885 | 0.36073 | 0.24097 | 0.3006 | 0.52555 | 0.53866 | 0.2725 | 0.34031 | 0.47638 | 0.63893 | 0.62509 | 0.2508 | 0.14584 | 0.12706 | 389.0364 | 336.4653
2013-02-05 | 23 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 27669.2446 | 19 | 78304.6847 | 17 | 2 | 5 | 404.4451 | 83.279 | 180 | 3.296 | 17 | 1250 | 82389.7673 | 8289.2664 | 286.8315 | 11.1753 | 14.0091 | 37 | 29.1015 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 7.8985 | 180 | 2.8338 | 12.6903 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0747 | 482.0887 | 1159.742 |  | 677.6534 | 10985.0332 | 3262.6952 | 1152.8852 | 0.22779 | 16.8724 | 23.133 | 0.02 | 0.05 | 30 | 165 | 453 | 677.4451 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 542.9415 | 26.8671 | 1.1255 | 1.0208 | 204.6534 | 473 | 438 | 446.1329 | 231.3122 | 0.2189 | 0.027 | 1.06 | 12.0767 | 12.0767 | 677.4451 | 677.6534 | 1.1255 | 1.1255 | 2.9126 | 2.9153 | 677.4451 | 677.6534 | 12.8057 | 1.1255 | 1.1255 | 298.15 | 1.9398 | 1.9416 | 677.4451 | 6.4221 | 1.1255 | 298.15 | 0.97281 | 0.9737 | 3.2627 | 4.1212 | 23.133 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.087139 | 0.087139 | 12.8057 | 435 | 446.1329 | 1.0625 | 1.066 | 298.15 | 0.3296 | 0.37978 | 0.91555 | 453 | 2816.5993 | 6.5855 | 0.78533 | 1.1013 | 21.47 | 121.8773 | 0.41238 | 0.076786 | 0.076786 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 80.3128 | 46.8542 | 0.16241 | 0.24753 | 0.75537 | 80.3128 | 58.7139 | 0.20193 | 0.25381 | 0.77452 | 5.9014 | 5.0402 | 0.912 | 0.5476 | 0.78693 | 1.1158 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 50.8122 | 0.18292 | 40.2181 | 0.14479 | 9.1213 | 0.032837 | 0.11546 | 10.2376 | 0.036855 | 0.12959 | 0.085021 | 0.072615 | 306.0765 | 261.4126 | 0.0087507 | 0.0052543 | 31.5026 | 18.9154 | 0.017414 | 0.016487 | 62.689 | 59.3528 | 9.1641 | 9.1614 | 3.2627 | 4.1259 | 1.56 | 1.5618 | 0.69819 | 1.0142 | 0.78533 | 1.1013 | 0.24753 | 0.75537 | 19.2278 | 3262.6952 | 4121.1803 | 0.91555 | 1.2839 | 80.3128 | 245.0826 | 0.28637 | 0.36173 | 0.21586 | 0.30272 | 0.52429 | 0.53496 | 0.27016 | 0.34125 | 0.43361 | 0.64937 | 0.68588 | 0.3152 | 0.14479 | 0.12959 | 400.2681 | 339.6808
2013-02-06 | 24 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 27843.6605 | 19 | 79180.8719 | 17 | 2 | 5 | 405.0192 | 83.5733 | 180 | 3.2618 | 17 | 1250 | 82509.6558 | 8917.8769 | 332.4934 | 11.6795 | 14.3666 | 37 | 29.4876 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 7.5124 | 180 | 2.687 | 12.6913 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.075 | 483.3832 | 1162.8563 |  | 679.473 | 11015.3534 | 3299.203 | 1160.1525 | 0.22923 | 19.5584 | 23.2148 | 0.02 | 0.05 | 30 | 165 | 453 | 678.0192 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 537.3138 | 26.5866 | 1.1256 | 1.0209 | 206.473 | 473 | 438 | 446.4134 | 231.6059 | 0.2189 | 0.027 | 1.06 | 12.1528 | 12.1528 | 678.0192 | 679.473 | 1.1256 | 1.126 | 2.9202 | 2.9388 | 678.0192 | 679.473 | 12.8067 | 1.1256 | 1.126 | 298.15 | 1.9448 | 1.9573 | 678.0192 | 6.4226 | 1.1256 | 298.15 | 0.97534 | 0.98158 | 3.2992 | 4.1515 | 23.2148 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.087447 | 0.087447 | 12.8067 | 435 | 446.4134 | 1.0625 | 1.066 | 298.15 | 0.32962 | 0.38111 | 0.90606 | 453 | 2816.5993 | 6.5855 | 0.77719 | 1.1114 | 21.47 | 123.4931 | 0.41777 | 0.077015 | 0.077015 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 93.0982 | 48.9646 | 0.16944 | 0.28823 | 0.81883 | 93.0982 | 60.2102 | 0.20691 | 0.29513 | 0.83843 | 5.9334 | 5.0625 | 0.92548 | 0.55226 | 0.77964 | 1.1265 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 50.5492 | 0.18198 | 40.1068 | 0.14438 | 9.4019 | 0.033847 | 0.11901 | 10.332 | 0.037195 | 0.13079 | 0.085483 | 0.072935 | 307.7384 | 262.5657 | 0.00888 | 0.005299 | 31.9681 | 19.0763 | 0.017518 | 0.016639 | 63.0653 | 59.8996 | 9.2326 | 9.214 | 3.2992 | 4.1846 | 1.5637 | 1.5762 | 0.68975 | 1.0239 | 0.77719 | 1.1114 | 0.28823 | 0.81883 | 19.2292 | 3299.203 | 4151.5006 | 0.90606 | 1.2956 | 93.0982 | 264.4796 | 0.28777 | 0.3621 | 0.21229 | 0.30356 | 0.56322 | 0.53361 | 0.27148 | 0.34161 | 0.42703 | 0.64962 | 0.73679 | 0.37087 | 0.14438 | 0.13079 | 402.7718 | 341.5416
2013-02-07 | 25 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 26614.8028 | 19 | 73831.5058 | 17 | 2 | 5 | 408.2311 | 83.6206 | 180 | 3.2874 | 17 | 1250 | 82915.2886 | 8401.8024 | 282.755 | 10.9405 | 13.8718 | 37 | 29.2851 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 7.7149 | 180 | 2.9314 | 12.6846 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0728 | 474.2584 | 1140.905 |  | 666.6466 | 10801.7304 | 3076.3127 | 1108.9501 | 0.21911 | 16.6326 | 23.228 | 0.02 | 0.05 | 30 | 165 | 453 | 681.2311 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 541.5254 | 26.8091 | 1.1265 | 1.0215 | 193.6466 | 473 | 438 | 446.1909 | 235.0402 | 0.2189 | 0.027 | 1.06 | 11.6165 | 11.6165 | 681.2311 | 666.6466 | 1.1265 | 1.1226 | 2.9599 | 2.7742 | 681.2311 | 666.6466 | 12.7999 | 1.1265 | 1.1226 | 298.15 | 1.9713 | 1.8476 | 681.2311 | 6.4192 | 1.1265 | 298.15 | 0.98861 | 0.92657 | 3.0763 | 3.9379 | 23.228 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.087497 | 0.087497 | 12.7999 | 435 | 446.1909 | 1.0625 | 1.066 | 298.15 | 0.32945 | 0.37988 | 0.91316 | 453 | 2816.5993 | 6.5855 | 0.78329 | 1.0426 | 21.47 | 122.6458 | 0.41494 | 0.076895 | 0.076895 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 79.1714 | 45.8715 | 0.15914 | 0.2435 | 0.68446 | 79.1714 | 58.1397 | 0.20001 | 0.2499 | 0.70244 | 5.5802 | 4.9044 | 0.94607 | 0.51265 | 0.78512 | 1.056 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 51.5138 | 0.18545 | 40.9227 | 0.14732 | 8.8382 | 0.031817 | 0.11188 | 9.8678 | 0.035524 | 0.12491 | 0.080394 | 0.070658 | 289.4196 | 254.3681 | 0.0090776 | 0.0049189 | 32.6793 | 17.7081 | 0.017776 | 0.015571 | 63.9946 | 56.0553 | 8.6565 | 8.8423 | 3.0763 | 3.6057 | 1.5914 | 1.4677 | 0.69579 | 0.95507 | 0.78329 | 1.0426 | 0.2435 | 0.68446 | 19.2191 | 3076.3127 | 3937.8775 | 0.91316 | 1.2154 | 79.1714 | 222.5404 | 0.28071 | 0.35933 | 0.22381 | 0.2979 | 0.52804 | 0.58654 | 0.26482 | 0.33899 | 0.42378 | 0.65072 | 0.65651 | 0.31087 | 0.14732 | 0.12491 | 386.0935 | 328.1315
2013-02-08 | 26 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 27413.0205 | 19 | 71538.4947 | 17 | 2 | 5 | 406.6409 | 80.7981 | 180 | 3.1607 | 17 | 1250 | 82208.7128 | 8195.2407 | 287.6129 | 10.8573 | 13.6646 | 37 | 29.5239 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 7.4761 | 180 | 2.8073 | 12.6889 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0742 | 480.1866 | 1155.1663 |  | 674.9797 | 10940.4915 | 2980.7706 | 1142.2092 | 0.22568 | 16.9184 | 22.4439 | 0.02 | 0.05 | 30 | 165 | 453 | 679.6409 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 520.6539 | 25.767 | 1.126 | 1.021 | 201.9797 | 473 | 438 | 447.233 | 232.4079 | 0.2189 | 0.027 | 1.06 | 11.9649 | 11.9649 | 679.6409 | 674.9797 | 1.126 | 1.1248 | 2.9405 | 2.8808 | 679.6409 | 674.9797 | 12.8043 | 1.126 | 1.1248 | 298.15 | 1.9583 | 1.9186 | 679.6409 | 6.4214 | 1.126 | 298.15 | 0.98212 | 0.96218 | 2.9808 | 4.0766 | 22.4439 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.084543 | 0.084543 | 12.8043 | 435 | 447.233 | 1.0624 | 1.0662 | 298.15 | 0.32954 | 0.38483 | 0.87797 | 453 | 2816.5993 | 6.5855 | 0.7531 | 1.0874 | 21.47 | 123.6451 | 0.41827 | 0.077036 | 0.077036 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 80.5316 | 45.5235 | 0.15798 | 0.2475 | 0.75829 | 80.5316 | 57.2724 | 0.19712 | 0.25374 | 0.77739 | 6.0436 | 5.0075 | 0.96026 | 0.53091 | 0.7549 | 1.1021 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 54.9429 | 0.19779 | 40.3843 | 0.14538 | 9.0611 | 0.03262 | 0.1147 | 10.1631 | 0.036587 | 0.12865 | 0.08707 | 0.072142 | 313.4535 | 259.7124 | 0.0092137 | 0.0050941 | 33.1695 | 18.3389 | 0.017647 | 0.016172 | 63.5298 | 58.221 | 9.0244 | 9.0841 | 2.9808 | 3.9704 | 1.5735 | 1.5338 | 0.66855 | 1.0028 | 0.7531 | 1.0874 | 0.2475 | 0.75829 | 19.2257 | 2980.7706 | 4076.6387 | 0.87797 | 1.2677 | 80.5316 | 246.7298 | 0.26407 | 0.36116 | 0.20893 | 0.30167 | 0.51948 | 0.57631 | 0.24913 | 0.34072 | 0.41045 | 0.65385 | 0.69735 | 0.32865 | 0.14538 | 0.12865 | 410.1528 | 336.2723
2013-02-10 | 27 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 30221.4393 | 19 | 76387.6647 | 17 | 2 | 5 | 326.6701 | 52.7674 | 180 | 2.097 | 17 | 1250 | 49399.7043 | 5483.2014 | 184.6996 | 12.1381 | 14.4977 | 37 | 28.2132 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 8.7868 | 180 | 2.3596 | 12.7042 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0794 | 501.0121 | 1205.2654 |  | 704.2533 | 11428.7035 | 3182.8194 | 1259.2266 | 0.2488 | 10.8647 | 14.6576 | 0.02 | 0.05 | 30 | 165 | 453 | 599.6701 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 345.4323 | 17.0748 | 1.1047 | 1.0069 | 231.2533 | 473 | 438 | 455.9252 | 143.7449 | 0.2189 | 0.027 | 1.06 | 13.1906 | 13.1906 | 599.6701 | 704.2533 | 1.1047 | 1.1327 | 1.9814 | 3.2667 | 599.6701 | 704.2533 | 12.8197 | 1.1047 | 1.1327 | 298.15 | 1.3196 | 2.1756 | 599.6701 | 6.4291 | 1.1047 | 298.15 | 0.66179 | 1.0911 | 3.1828 | 4.5649 | 14.6576 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.055213 | 0.055213 | 12.8197 | 435 | 455.9252 | 1.0618 | 1.0683 | 298.15 | 0.32973 | 0.42649 | 0.58249 | 453 | 2816.5993 | 6.5855 | 0.49965 | 1.2229 | 21.47 | 118.1598 | 0.4 | 0.07626 | 0.07626 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 51.7159 | 50.8839 | 0.17584 | 0.16077 | 1.0155 | 51.7159 | 60.759 | 0.20874 | 0.16413 | 1.0368 | 8.0264 | 5.3591 | 0.54545 | 0.58147 | 0.49781 | 1.2389 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 61.3447 | 0.22084 | 38.7157 | 0.13938 | 8.5701 | 0.030852 | 0.10848 | 11.1491 | 0.040137 | 0.14113 | 0.11564 | 0.077208 | 416.2916 | 277.9491 | 0.0052336 | 0.0055792 | 18.8409 | 20.0851 | 0.010639 | 0.017807 | 38.2992 | 64.1068 | 11.2092 | 9.9239 | 3.1828 | 6.9505 | 0.89312 | 1.7491 | 0.44443 | 1.1677 | 0.49965 | 1.2229 | 0.16077 | 1.0155 | 19.2488 | 3182.8194 | 4564.8506 | 0.58249 | 1.4257 | 51.7159 | 326.6761 | 0.25577 | 0.36683 | 0.12576 | 0.30779 | 0.57841 | 0.3492 | 0.24129 | 0.34607 | 0.44898 | 0.66757 | 0.83043 | 0.32176 | 0.13938 | 0.14113 | 473.4317 | 362.141
2013-02-13 | 28 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 33251.8992 | 19 | 74478.4711 | 17 | 2 | 5 | 413.7782 | 84.7692 | 180 | 3.2875 | 17 | 1250 | 83530.8966 | 8231.7834 | 258.5374 | 11.1754 | 13.842 | 37 | 29.5082 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 7.4918 | 180 | 2.6666 | 12.7207 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.085 | 523.4281 | 1259.1906 |  | 735.7625 | 11955.5147 | 3103.2696 | 1385.4958 | 0.27375 | 15.2081 | 23.547 | 0.02 | 0.05 | 30 | 165 | 453 | 686.7782 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 541.5453 | 26.7341 | 1.128 | 1.0224 | 262.7625 | 473 | 438 | 446.2659 | 240.5123 | 0.2189 | 0.027 | 1.06 | 14.5133 | 14.5133 | 686.7782 | 735.7625 | 1.128 | 1.1412 | 3.0403 | 3.7015 | 686.7782 | 735.7625 | 12.8363 | 1.128 | 1.1412 | 298.15 | 2.0248 | 2.4652 | 686.7782 | 6.4374 | 1.128 | 298.15 | 1.0155 | 1.2363 | 3.1033 | 5.0917 | 23.547 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.088699 | 0.088699 | 12.8363 | 435 | 446.2659 | 1.0625 | 1.066 | 298.15 | 0.33038 | 0.38131 | 0.91319 | 453 | 2816.5993 | 6.5855 | 0.78331 | 1.4206 | 21.47 | 123.5797 | 0.41805 | 0.077027 | 0.077027 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 72.3905 | 46.8548 | 0.16241 | 0.22312 | 1.1024 | 72.3905 | 58.0147 | 0.1996 | 0.22844 | 1.1287 | 8.3698 | 5.7201 | 0.99984 | 0.75204 | 0.7842 | 1.4424 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 64.1419 | 0.23091 | 37.2222 | 0.134 | 10.3179 | 0.037144 | 0.13061 | 12.1031 | 0.043571 | 0.1532 | 0.12058 | 0.08241 | 434.0992 | 296.675 | 0.0095935 | 0.0072159 | 34.5367 | 25.9772 | 0.018355 | 0.021655 | 66.0791 | 77.9588 | 11.473 | 10.8118 | 3.1033 | 6.2105 | 1.6435 | 2.0839 | 0.69462 | 1.3319 | 0.78331 | 1.4206 | 0.22312 | 1.1024 | 19.2737 | 3103.2696 | 5091.6619 | 0.91319 | 1.6561 | 72.3905 | 357.6608 | 0.22665 | 0.37188 | 0.17921 | 0.325 | 0.51354 | 0.52964 | 0.21382 | 0.35083 | 0.40993 | 0.63912 | 0.77599 | 0.28484 | 0.134 | 0.1532 | 534.7149 | 400.6111
2013-02-14 | 29 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 32774.0437 | 19 | 75137.9764 | 17 | 2 | 5 | 412.6248 | 84.2967 | 180 | 3.2945 | 17 | 1250 | 85472.5401 | 7900.679 | 237.6555 | 10.856 | 13.9308 | 37 | 29.3517 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 7.6483 | 180 | 3.0748 | 12.7181 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0841 | 519.8973 | 1250.6967 |  | 730.7994 | 11872.4449 | 3130.749 | 1365.5852 | 0.26981 | 13.9797 | 23.4158 | 0.02 | 0.05 | 30 | 165 | 453 | 685.6248 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 542.6909 | 26.7961 | 1.1277 | 1.0222 | 257.7994 | 473 | 438 | 446.2039 | 239.421 | 0.2189 | 0.027 | 1.06 | 14.3048 | 14.3048 | 685.6248 | 730.7994 | 1.1277 | 1.1398 | 3.0247 | 3.6318 | 685.6248 | 730.7994 | 12.8337 | 1.1277 | 1.1398 | 298.15 | 2.0144 | 2.4187 | 685.6248 | 6.4361 | 1.1277 | 298.15 | 1.0102 | 1.213 | 3.1307 | 5.0086 | 23.4158 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.088204 | 0.088204 | 12.8337 | 435 | 446.2039 | 1.0625 | 1.066 | 298.15 | 0.33032 | 0.38094 | 0.91513 | 453 | 2816.5993 | 6.5855 | 0.78497 | 1.3931 | 21.47 | 122.9247 | 0.41587 | 0.076934 | 0.076934 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 66.5435 | 45.5179 | 0.15796 | 0.20451 | 0.92833 | 66.5435 | 58.3865 | 0.20084 | 0.21015 | 0.95394 | 8.1493 | 5.6644 | 0.98734 | 0.73293 | 0.78609 | 1.4142 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 62.6911 | 0.22569 | 37.4404 | 0.13479 | 10.0007 | 0.036003 | 0.12659 | 11.8789 | 0.042764 | 0.15037 | 0.11741 | 0.081607 | 422.6672 | 293.7859 | 0.0094736 | 0.0070325 | 34.1051 | 25.317 | 0.018231 | 0.02119 | 65.6301 | 76.2857 | 11.2801 | 10.673 | 3.1307 | 6.0402 | 1.6335 | 2.0378 | 0.69677 | 1.3049 | 0.78497 | 1.3931 | 0.20451 | 0.92833 | 19.2698 | 3130.749 | 5008.5921 | 0.91513 | 1.6241 | 66.5435 | 302.0618 | 0.23199 | 0.37114 | 0.1822 | 0.32335 | 0.48168 | 0.64376 | 0.21886 | 0.35013 | 0.41373 | 0.64033 | 0.66639 | 0.26053 | 0.13479 | 0.15037 | 522.4024 | 395.3887
2013-02-15 | 30 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 32584.6372 | 19 | 73256.3161 | 17 | 2 | 5 | 411.4297 | 83.9321 | 180 | 3.3417 | 17 | 1250 | 85530.1844 | 7711.459 | 308.5578 | 11.4657 | 13.9025 | 37 | 29.4315 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 7.5685 | 180 | 2.4368 | 12.717 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0838 | 518.4974 | 1247.329 |  | 728.8317 | 11839.5187 | 3052.3465 | 1357.6932 | 0.26826 | 18.1505 | 23.3145 | 0.02 | 0.05 | 30 | 165 | 453 | 684.4297 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 550.4708 | 27.1825 | 1.1273 | 1.0221 | 255.8317 | 473 | 438 | 445.8175 | 238.6122 | 0.2189 | 0.027 | 1.06 | 14.2221 | 14.2221 | 684.4297 | 728.8317 | 1.1273 | 1.1393 | 3.0089 | 3.6042 | 684.4297 | 728.8317 | 12.8327 | 1.1273 | 1.1393 | 298.15 | 2.0039 | 2.4004 | 684.4297 | 6.4356 | 1.1273 | 298.15 | 1.005 | 1.2038 | 3.0523 | 4.9757 | 23.3145 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.087823 | 0.087823 | 12.8327 | 435 | 445.8175 | 1.0625 | 1.0659 | 298.15 | 0.3303 | 0.37913 | 0.92825 | 453 | 2816.5993 | 6.5855 | 0.79622 | 1.3819 | 21.47 | 123.2587 | 0.41698 | 0.076981 | 0.076981 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 86.3962 | 48.0698 | 0.16646 | 0.26698 | 1.1689 | 86.3962 | 58.2681 | 0.20044 | 0.27278 | 1.1943 | 8.1608 | 5.6422 | 0.96523 | 0.72716 | 0.79755 | 1.4029 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 63.9856 | 0.23035 | 37.5285 | 0.1351 | 10.507 | 0.037825 | 0.133 | 11.9244 | 0.042928 | 0.15094 | 0.11757 | 0.081287 | 423.2638 | 292.6343 | 0.0092614 | 0.0069772 | 33.341 | 25.1178 | 0.018079 | 0.021024 | 65.0859 | 75.6872 | 11.2132 | 10.6179 | 3.0523 | 5.9896 | 1.6248 | 2.0213 | 0.7084 | 1.2941 | 0.79622 | 1.3819 | 0.26698 | 1.1689 | 19.2683 | 3052.3465 | 4975.6659 | 0.92825 | 1.6111 | 86.3962 | 378.2671 | 0.2275 | 0.37085 | 0.18589 | 0.32263 | 0.46983 | 0.45489 | 0.21462 | 0.34985 | 0.42327 | 0.64025 | 0.84584 | 0.3353 | 0.1351 | 0.15094 | 521.6907 | 393.4393
2013-02-17 | 31 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 34548.6904 | 19 | 79296.1336 | 17 | 2 | 5 | 400.0393 | 99.9213 | 180 | 3.9469 | 17 | 1250 | 93489.8528 | 6547.6718 | 299.7724 | 12.43 | 14.8586 | 37 | 30.1043 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 6.8957 | 180 | 2.4286 | 12.7277 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0874 | 533.0026 | 1282.2236 |  | 749.221 | 12180.9472 | 3304.0056 | 1439.5288 | 0.28442 | 17.6337 | 27.7559 | 0.02 | 0.05 | 30 | 165 | 453 | 673.0393 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 650.1636 | 32.0784 | 1.1243 | 1.0209 | 276.221 | 473 | 438 | 440.9216 | 232.1177 | 0.2189 | 0.027 | 1.06 | 15.0793 | 15.0793 | 673.0393 | 749.221 | 1.1243 | 1.1448 | 2.8648 | 3.8932 | 673.0393 | 749.221 | 12.8434 | 1.1243 | 1.1448 | 298.15 | 1.9079 | 2.5929 | 673.0393 | 6.441 | 1.1243 | 298.15 | 0.95683 | 1.3003 | 3.304 | 5.3171 | 27.7559 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.10455 | 0.10455 | 12.8434 | 435 | 440.9216 | 1.0629 | 1.0647 | 298.15 | 0.33069 | 0.3571 | 1.0964 | 453 | 2816.5993 | 6.5855 | 0.94042 | 1.4893 | 21.47 | 126.0744 | 0.42637 | 0.07738 | 0.07738 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 83.9363 | 52.1054 | 0.17991 | 0.26161 | 1.3096 | 83.9363 | 62.2694 | 0.21377 | 0.26723 | 1.3377 | 8.9106 | 5.869 | 0.74138 | 0.85106 | 0.94196 | 1.5133 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 63.4784 | 0.22852 | 36.6584 | 0.13197 | 10.948 | 0.039413 | 0.13858 | 12.5663 | 0.045239 | 0.15907 | 0.12837 | 0.084555 | 462.1479 | 304.3979 | 0.0071136 | 0.008166 | 25.6088 | 29.3976 | 0.017055 | 0.023445 | 61.3967 | 84.4016 | 12.2146 | 11.1861 | 3.304 | 7.0581 | 1.5508 | 2.2358 | 0.83587 | 1.3847 | 0.94042 | 1.4893 | 0.26161 | 1.3096 | 19.2844 | 3304.0056 | 5317.0944 | 1.0964 | 1.7362 | 83.9363 | 420.1705 | 0.23225 | 0.37376 | 0.20709 | 0.32795 | 0.36496 | 0.52284 | 0.21911 | 0.35261 | 0.52996 | 0.61934 | 0.87933 | 0.27818 | 0.13197 | 0.15907 | 549.1534 | 418.1972
2013-02-18 | 32 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 33449.4607 | 19 | 74706.4825 | 17 | 2 | 5 | 405.6689 | 83.3383 | 180 | 3.284 | 17 | 1250 | 86197.8079 | 6296.7087 | 263.8362 | 12.1442 | 14.4889 | 37 | 30.0187 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 6.9813 | 180 | 2.3447 | 12.7217 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0854 | 524.8874 | 1262.7012 |  | 737.8138 | 11989.8586 | 3112.7701 | 1393.7275 | 0.27538 | 15.5198 | 23.1495 | 0.02 | 0.05 | 30 | 165 | 453 | 678.6689 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 540.9638 | 26.7032 | 1.1258 | 1.021 | 264.8138 | 473 | 438 | 446.2968 | 232.372 | 0.2189 | 0.027 | 1.06 | 14.5996 | 14.5996 | 678.6689 | 737.8138 | 1.1258 | 1.1417 | 2.9355 | 3.7305 | 678.6689 | 737.8138 | 12.8374 | 1.1258 | 1.1417 | 298.15 | 1.9551 | 2.4845 | 678.6689 | 6.438 | 1.1258 | 298.15 | 0.98047 | 1.246 | 3.1128 | 5.126 | 23.1495 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.087201 | 0.087201 | 12.8374 | 435 | 446.2968 | 1.0625 | 1.066 | 298.15 | 0.33041 | 0.38148 | 0.91221 | 453 | 2816.5993 | 6.5855 | 0.78247 | 1.429 | 21.47 | 125.7159 | 0.42517 | 0.077329 | 0.077329 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 73.8741 | 50.9094 | 0.17592 | 0.22966 | 1.2879 | 73.8741 | 60.7221 | 0.20862 | 0.23444 | 1.3147 | 8.5512 | 5.743 | 0.92939 | 0.76124 | 0.78312 | 1.4517 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 64.8301 | 0.23339 | 37.1337 | 0.13368 | 10.413 | 0.037487 | 0.13181 | 12.2247 | 0.044009 | 0.15474 | 0.1232 | 0.08274 | 443.5116 | 297.8626 | 0.0089176 | 0.0073041 | 32.1033 | 26.2948 | 0.017558 | 0.021831 | 63.21 | 78.5914 | 11.664 | 10.869 | 3.1128 | 6.477 | 1.5736 | 2.1031 | 0.69527 | 1.3418 | 0.78247 | 1.429 | 0.22966 | 1.2879 | 19.2754 | 3112.7701 | 5126.0057 | 0.91221 | 1.666 | 73.8741 | 414.2607 | 0.226 | 0.37217 | 0.17796 | 0.32501 | 0.38066 | 0.48607 | 0.21321 | 0.35111 | 0.42795 | 0.63803 | 0.90123 | 0.29351 | 0.13368 | 0.15474 | 538.8249 | 402.7487
2013-02-21 | 33 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 32821.181 | 19 | 72061.89 | 17 | 2 | 5 | 413.5924 | 90.1577 | 180 | 3.5599 | 17 | 1250 | 54587.5947 | 3923.2092 | 281.7501 | 16.4842 | 17.6759 | 37 | 28.7913 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 8.2087 | 180 | 1.1917 | 12.7183 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0842 | 520.2456 | 1251.5347 |  | 731.2891 | 11880.6392 | 3002.5787 | 1367.5492 | 0.2702 | 16.5735 | 25.0438 | 0.02 | 0.05 | 30 | 165 | 453 | 686.5924 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 586.424 | 28.9549 | 1.1279 | 1.0228 | 258.2891 | 473 | 438 | 444.0451 | 242.5473 | 0.2189 | 0.027 | 1.06 | 14.3253 | 14.3253 | 686.5924 | 731.2891 | 1.1279 | 1.14 | 3.0373 | 3.6386 | 686.5924 | 731.2891 | 12.834 | 1.1279 | 1.14 | 298.15 | 2.0229 | 2.4233 | 686.5924 | 6.4362 | 1.1279 | 298.15 | 1.0145 | 1.2153 | 3.0026 | 5.0168 | 25.0438 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.094337 | 0.094337 | 12.834 | 435 | 444.0451 | 1.0627 | 1.0655 | 298.15 | 0.33037 | 0.37102 | 0.98887 | 453 | 2816.5993 | 6.5855 | 0.84823 | 1.3961 | 21.47 | 120.5792 | 0.40806 | 0.076602 | 0.076602 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 78.89 | 69.0727 | 0.23644 | 0.2547 | 2.49 | 78.89 | 74.0602 | 0.25306 | 0.25729 | 2.5153 | 8.2854 | 5.6699 | 0.93859 | 0.75056 | 0.84596 | 1.4166 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 65.4052 | 0.23546 | 37.4186 | 0.13471 | 10.4832 | 0.037739 | 0.1327 | 12.2075 | 0.043947 | 0.15453 | 0.11937 | 0.081687 | 429.7257 | 294.0719 | 0.0090058 | 0.0072017 | 32.421 | 25.9261 | 0.018223 | 0.021429 | 65.6018 | 77.144 | 11.288 | 10.6867 | 3.0026 | 6.0375 | 1.6518 | 2.0523 | 0.75389 | 1.3017 | 0.84823 | 1.3961 | 0.2547 | 2.49 | 19.2702 | 3002.5787 | 5016.7863 | 0.98887 | 1.6276 | 78.89 | 771.2465 | 0.22218 | 0.37122 | 0.1966 | 0.32358 | 0.37452 | 0.16209 | 0.2096 | 0.3502 | 0.44544 | 0.63428 | 1.7836 | 0.30027 | 0.13471 | 0.15453 | 527.7485 | 397.1421
2013-02-25 | 34 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 26444.552 | 19 | 72782.9339 | 17 | 2 | 5 | 377.9695 | 96.0796 | 180 | 4.1023 | 17 | 1250 | 32538.3839 | 3177.801 | 171.6663 | 13.9554 | 15.4214 | 37 | 27.0746 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 9.9254 | 180 | 1.466 | 12.6837 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0724 | 472.9934 | 1137.8619 |  | 664.8685 | 10772.1342 | 3032.6222 | 1101.8563 | 0.21771 | 10.098 | 26.6888 | 0.02 | 0.05 | 30 | 165 | 453 | 650.9695 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 675.7714 | 33.4577 | 1.1183 | 1.0174 | 191.8685 | 473 | 438 | 439.5423 | 211.4272 | 0.2189 | 0.027 | 1.06 | 11.5422 | 11.5422 | 650.9695 | 664.8685 | 1.1183 | 1.1221 | 2.5791 | 2.7516 | 650.9695 | 664.8685 | 12.799 | 1.1183 | 1.1221 | 298.15 | 1.7177 | 1.8326 | 650.9695 | 6.4187 | 1.1183 | 298.15 | 0.86143 | 0.91904 | 3.0326 | 3.9083 | 26.6888 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.10053 | 0.10053 | 12.799 | 435 | 439.5423 | 1.063 | 1.0644 | 298.15 | 0.32957 | 0.34969 | 1.1395 | 453 | 2816.5993 | 6.5855 | 0.97746 | 1.0255 | 21.47 | 113.3947 | 0.38412 | 0.075586 | 0.075586 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 48.0666 | 58.4892 | 0.20118 | 0.15183 | 1.2745 | 48.0666 | 64.6246 | 0.22162 | 0.15377 | 1.2908 | 5.9304 | 4.8822 | 0.51121 | 0.55795 | 0.97353 | 1.0359 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 53.7118 | 0.19336 | 41.0418 | 0.14775 | 7.7388 | 0.02786 | 0.09796 | 10.0861 | 0.03631 | 0.12767 | 0.085439 | 0.070339 | 307.5804 | 253.2188 | 0.0049051 | 0.0053536 | 17.6582 | 19.2728 | 0.014786 | 0.015935 | 53.2314 | 57.3675 | 8.963 | 8.7905 | 3.0326 | 4.2248 | 1.368 | 1.4829 | 0.87693 | 0.92494 | 0.97746 | 1.0255 | 0.15183 | 1.2745 | 19.2177 | 3032.6222 | 3908.2813 | 1.1395 | 1.1955 | 48.0666 | 403.4652 | 0.27851 | 0.35893 | 0.28109 | 0.2949 | 0.50893 | 0.16374 | 0.26274 | 0.33861 | 0.63173 | 0.62374 | 1.2428 | 0.15533 | 0.14775 | 0.12767 | 378.47 | 329.859
2013-02-26 | 35 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 26256.5736 | 19 | 73762.7408 | 17 | 2 | 5 | 408.858 | 118.8484 | 180 | 4.7913 | 17 | 1250 | 86545.398 | 12437.3086 | 364.2816 | 10.1163 | 13.7564 | 37 | 29.3386 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 7.6614 | 180 | 3.6401 | 12.6827 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0721 | 471.5966 | 1134.5015 |  | 662.905 | 10739.4563 | 3073.4475 | 1094.0239 | 0.21616 | 21.4283 | 33.0135 | 0.02 | 0.05 | 30 | 165 | 453 | 681.858 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 789.2691 | 39.0801 | 1.1266 | 1.0238 | 189.905 | 473 | 438 | 433.9199 | 247.9381 | 0.2189 | 0.027 | 1.06 | 11.4601 | 11.4601 | 681.858 | 662.905 | 1.1266 | 1.1215 | 2.9675 | 2.7268 | 681.858 | 662.905 | 12.798 | 1.1266 | 1.1215 | 298.15 | 1.9764 | 1.816 | 681.858 | 6.4182 | 1.1266 | 298.15 | 0.99116 | 0.91075 | 3.0734 | 3.8756 | 33.0135 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.12436 | 0.12436 | 12.798 | 435 | 433.9199 | 1.0634 | 1.0631 | 298.15 | 0.32967 | 0.32496 | 1.3309 | 453 | 2816.5993 | 6.5855 | 1.1416 | 1.0224 | 21.47 | 122.8698 | 0.41569 | 0.076926 | 0.076926 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 101.9988 | 42.4221 | 0.14764 | 0.31139 | 0.53483 | 101.9988 | 57.6563 | 0.1984 | 0.32163 | 0.55241 | 5.4191 | 4.8577 | 0.62944 | 0.59303 | 1.1473 | 1.0355 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 50.7931 | 0.18286 | 41.1751 | 0.14823 | 9.0966 | 0.032748 | 0.11515 | 9.5996 | 0.034559 | 0.12151 | 0.078073 | 0.069985 | 281.0634 | 251.9459 | 0.0060395 | 0.0056902 | 21.7423 | 20.4846 | 0.01782 | 0.016496 | 64.1535 | 59.3861 | 8.4926 | 8.7333 | 3.0734 | 3.444 | 1.6514 | 1.4911 | 1.0173 | 0.89806 | 1.1416 | 1.0224 | 0.31139 | 0.53483 | 19.2162 | 3073.4475 | 3875.6034 | 1.3309 | 1.1919 | 101.9988 | 175.1856 | 0.28428 | 0.35847 | 0.33065 | 0.29612 | 0.74887 | 0.86668 | 0.26819 | 0.33818 | 0.61776 | 0.60228 | 0.5231 | 0.27276 | 0.14823 | 0.12151 | 366.9592 | 331.8165
2013-02-27 | 36 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 26151.1911 | 19 | 72830.675 | 17 | 2 | 5 | 406.5682 | 84.4147 | 180 | 3.3643 | 17 | 1250 | 77841.8785 | 11305.7834 | 328.7704 | 9.5117 | 13.9475 | 37 | 29.0194 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 7.9806 | 180 | 4.4357 | 12.6821 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0719 | 470.8133 | 1132.6174 |  | 661.8041 | 10721.1367 | 3034.6115 | 1089.633 | 0.21529 | 19.3394 | 23.4485 | 0.02 | 0.05 | 30 | 165 | 453 | 679.5682 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 554.1968 | 27.4419 | 1.126 | 1.0213 | 188.8041 | 473 | 438 | 445.5581 | 234.0101 | 0.2189 | 0.027 | 1.06 | 11.4141 | 11.4141 | 679.5682 | 661.8041 | 1.126 | 1.1213 | 2.9379 | 2.7129 | 679.5682 | 661.8041 | 12.7974 | 1.126 | 1.1213 | 298.15 | 1.9567 | 1.8068 | 679.5682 | 6.4179 | 1.126 | 298.15 | 0.98127 | 0.90611 | 3.0346 | 3.8573 | 23.4485 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.088328 | 0.088328 | 12.7974 | 435 | 445.5581 | 1.0626 | 1.0658 | 298.15 | 0.3294 | 0.37689 | 0.93453 | 453 | 2816.5993 | 6.5855 | 0.80161 | 1.0159 | 21.47 | 121.534 | 0.41124 | 0.076737 | 0.076737 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 92.0557 | 39.8922 | 0.13921 | 0.2795 | 0.4283 | 92.0557 | 58.4562 | 0.20107 | 0.29076 | 0.44556 | 5.4416 | 4.8439 | 0.91399 | 0.50235 | 0.80815 | 1.0284 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 51.3653 | 0.18492 | 41.2508 | 0.1485 | 8.9239 | 0.032126 | 0.11296 | 9.3854 | 0.033787 | 0.1188 | 0.078396 | 0.069786 | 282.2273 | 251.2305 | 0.0087698 | 0.00482 | 31.5711 | 17.3521 | 0.01769 | 0.015212 | 63.6852 | 54.7628 | 8.4762 | 8.7012 | 3.0346 | 3.4528 | 1.5798 | 1.4299 | 0.71329 | 0.92756 | 0.80161 | 1.0159 | 0.2795 | 0.4283 | 19.2153 | 3034.6115 | 3857.2839 | 0.93453 | 1.1843 | 92.0557 | 141.0632 | 0.28182 | 0.35822 | 0.2331 | 0.29541 | 0.75685 | 1.1958 | 0.26586 | 0.33794 | 0.43833 | 0.64869 | 0.4216 | 0.34868 | 0.1485 | 0.1188 | 377.4835 | 323.3454
2013-02-28 | 37 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 26229.9513 | 19 | 73583.6814 | 17 | 2 | 5 | 411.8763 | 134.1716 | 180 | 5.4246 | 17 | 1250 | 87746.0975 | 12182.0642 | 364.5709 | 9.8632 | 13.6389 | 37 | 30.1989 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 6.8011 | 180 | 3.7757 | 12.6825 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0721 | 471.3987 | 1134.0256 |  | 662.6269 | 10734.8283 | 3065.9867 | 1092.9146 | 0.21594 | 21.4453 | 37.2699 | 0.02 | 0.05 | 30 | 165 | 453 | 684.8763 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 893.594 | 44.2462 | 1.1275 | 1.0253 | 189.6269 | 473 | 438 | 428.7538 | 256.1225 | 0.2189 | 0.027 | 1.06 | 11.4485 | 11.4485 | 684.8763 | 662.6269 | 1.1275 | 1.1215 | 3.0065 | 2.7233 | 684.8763 | 662.6269 | 12.7978 | 1.1275 | 1.1215 | 298.15 | 2.0023 | 1.8137 | 684.8763 | 6.4181 | 1.1275 | 298.15 | 1.0042 | 0.90958 | 3.066 | 3.871 | 37.2699 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.14039 | 0.14039 | 12.7978 | 435 | 428.7538 | 1.0637 | 1.0618 | 298.15 | 0.32977 | 0.3029 | 1.5068 | 453 | 2816.5993 | 6.5855 | 1.2925 | 1.0216 | 21.47 | 126.4702 | 0.42768 | 0.077436 | 0.077436 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 102.0798 | 41.3632 | 0.14412 | 0.31093 | 0.52885 | 102.0798 | 57.1649 | 0.19677 | 0.32156 | 0.54693 | 5.376 | 4.8542 | 0.52042 | 0.62955 | 1.2991 | 1.0357 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 50.679 | 0.18244 | 41.1942 | 0.1483 | 9.0922 | 0.032732 | 0.11509 | 9.5835 | 0.034501 | 0.12131 | 0.077452 | 0.069935 | 278.8266 | 251.7653 | 0.0049935 | 0.0060406 | 17.9765 | 21.7461 | 0.018096 | 0.017037 | 65.145 | 61.3323 | 8.442 | 8.7252 | 3.066 | 3.3643 | 1.6994 | 1.5108 | 1.1521 | 0.88125 | 1.2925 | 1.0216 | 0.31093 | 0.52885 | 19.2159 | 3065.9867 | 3870.9754 | 1.5068 | 1.191 | 102.0798 | 173.6252 | 0.28388 | 0.35841 | 0.37473 | 0.29619 | 0.72347 | 1.2009 | 0.26781 | 0.33812 | 0.68885 | 0.5833 | 0.51765 | 0.24056 | 0.1483 | 0.12131 | 361.948 | 334.8437
2013-03-01 | 38 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 26383.5778 | 19 | 73732.6292 | 1 | 2 | 5 | 402.8019 | 83.5099 | 180 | 3.3592 | 17 | 1250 | 86707.9399 | 12090.7928 | 361.0251 | 9.503 | 13.0809 | 37 | 30.4024 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 6.5976 | 180 | 3.578 | 12.6834 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0723 | 472.5404 | 1136.772 |  | 664.2316 | 10761.5345 | 3072.1929 | 1099.3157 | 0.2172 | 21.2368 | 23.1972 | 0.02 | 0.05 | 30 | 165 | 453 | 675.8019 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 553.364 | 27.3979 | 1.125 | 1.0206 | 191.2316 | 473 | 438 | 445.6021 | 230.1998 | 0.2189 | 0.027 | 1.06 | 11.5155 | 11.5155 | 675.8019 | 664.2316 | 1.125 | 1.1219 | 2.89 | 2.7436 | 675.8019 | 664.2316 | 12.7987 | 1.125 | 1.1219 | 298.15 | 1.9247 | 1.8272 | 675.8019 | 6.4185 | 1.125 | 298.15 | 0.96526 | 0.91635 | 3.0722 | 3.8977 | 23.1972 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.087381 | 0.087381 | 12.7987 | 435 | 445.6021 | 1.0626 | 1.0658 | 298.15 | 0.32943 | 0.37713 | 0.93312 | 453 | 2816.5993 | 6.5855 | 0.80041 | 1.0281 | 21.47 | 127.322 | 0.43052 | 0.077556 | 0.077556 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 101.087 | 39.8554 | 0.13909 | 0.3069 | 0.56428 | 101.087 | 54.8297 | 0.18898 | 0.31687 | 0.58262 | 5.5534 | 4.8743 | 0.88228 | 0.50933 | 0.80648 | 1.0426 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 51.4375 | 0.18518 | 41.0848 | 0.14791 | 9.1026 | 0.03277 | 0.11522 | 9.6755 | 0.034832 | 0.12248 | 0.080007 | 0.070224 | 288.0259 | 252.8063 | 0.0084655 | 0.0048871 | 30.4757 | 17.5935 | 0.017313 | 0.015419 | 62.3274 | 55.5099 | 8.6255 | 8.772 | 3.0722 | 3.6342 | 1.5476 | 1.4501 | 0.71303 | 0.94075 | 0.80041 | 1.0281 | 0.3069 | 0.56428 | 19.2172 | 3072.1929 | 3897.6817 | 0.93312 | 1.1986 | 101.087 | 185.8621 | 0.28279 | 0.35878 | 0.23071 | 0.29634 | 0.72664 | 1.1415 | 0.26679 | 0.33847 | 0.44695 | 0.64876 | 0.54884 | 0.38343 | 0.14791 | 0.12248 | 380.829 | 325.9097
2013-03-03 | 40 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 26698.3551 | 19 | 75580.7192 | 17 | 2 | 5 | 401.2081 | 93.9534 | 180 | 3.7468 | 17 | 1250 | 87575.154 | 11218.4544 | 365.2231 | 11.262 | 14.7797 | 37 | 31.0763 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 5.9237 | 180 | 3.5177 | 12.6851 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0729 | 474.8791 | 1142.3982 |  | 667.5191 | 10816.255 | 3149.1966 | 1112.4315 | 0.2198 | 21.4837 | 26.0982 | 0.02 | 0.05 | 30 | 165 | 453 | 674.2081 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 617.2087 | 30.5549 | 1.1246 | 1.0209 | 194.5191 | 473 | 438 | 442.4451 | 231.763 | 0.2189 | 0.027 | 1.06 | 11.6529 | 11.6529 | 674.2081 | 667.5191 | 1.1246 | 1.1228 | 2.87 | 2.7853 | 674.2081 | 667.5191 | 12.8004 | 1.1246 | 1.1228 | 298.15 | 1.9115 | 1.855 | 674.2081 | 6.4194 | 1.1246 | 298.15 | 0.9586 | 0.93028 | 3.1492 | 3.9524 | 26.0982 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.098309 | 0.098309 | 12.8004 | 435 | 442.4451 | 1.0628 | 1.0651 | 298.15 | 0.32954 | 0.36278 | 1.0408 | 453 | 2816.5993 | 6.5855 | 0.89276 | 1.0455 | 21.47 | 130.1423 | 0.43992 | 0.077955 | 0.077955 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 102.2625 | 47.2172 | 0.16362 | 0.31543 | 0.60779 | 102.2625 | 61.9391 | 0.21267 | 0.32535 | 0.62691 | 5.6337 | 4.9153 | 0.78746 | 0.54497 | 0.89917 | 1.0612 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 50.8995 | 0.18324 | 40.8648 | 0.14711 | 9.2179 | 0.033184 | 0.11668 | 9.8188 | 0.035348 | 0.12429 | 0.081164 | 0.070814 | 292.1921 | 254.9309 | 0.0075557 | 0.0052291 | 27.2005 | 18.8246 | 0.017179 | 0.01604 | 61.8453 | 57.743 | 8.7829 | 8.8677 | 3.1492 | 3.8 | 1.5487 | 1.4922 | 0.79445 | 0.94724 | 0.89276 | 1.0455 | 0.31543 | 0.60779 | 19.2198 | 3149.1966 | 3952.4021 | 1.0408 | 1.2189 | 102.2625 | 197.0465 | 0.28646 | 0.35953 | 0.25429 | 0.29782 | 0.66754 | 1.4139 | 0.27025 | 0.33918 | 0.50221 | 0.63479 | 0.58132 | 0.35332 | 0.14711 | 0.12429 | 381.238 | 331.4985
2013-03-04 | 41 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 25926.0967 | 19 | 73776.0033 | 17 | 2 | 5 | 393.2528 | 79.0846 | 180 | 3.0989 | 17 | 1250 | 82950.6282 | 11465.3377 | 355.6419 | 10.1138 | 13.7226 | 37 | 29.9408 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 7.0592 | 180 | 3.6088 | 12.6809 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0715 | 469.1402 | 1128.5924 |  | 659.4522 | 10682.0066 | 3074.0001 | 1080.254 | 0.21344 | 20.9201 | 21.9679 | 0.02 | 0.05 | 30 | 165 | 453 | 666.2528 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 510.4716 | 25.2792 | 1.1224 | 1.0186 | 186.4522 | 473 | 438 | 447.7208 | 218.532 | 0.2189 | 0.027 | 1.06 | 11.3159 | 11.3159 | 666.2528 | 659.4522 | 1.1224 | 1.1206 | 2.7684 | 2.6833 | 666.2528 | 659.4522 | 12.7962 | 1.1224 | 1.1206 | 298.15 | 1.8438 | 1.7871 | 666.2528 | 6.4173 | 1.1224 | 298.15 | 0.92465 | 0.89624 | 3.074 | 3.8182 | 21.9679 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.08275 | 0.08275 | 12.7962 | 435 | 447.7208 | 1.0624 | 1.0663 | 298.15 | 0.32932 | 0.38685 | 0.8608 | 453 | 2816.5993 | 6.5855 | 0.73837 | 0.99995 | 21.47 | 125.3898 | 0.42409 | 0.077283 | 0.077283 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 99.5797 | 42.412 | 0.14761 | 0.304 | 0.53548 | 99.5797 | 57.5151 | 0.19793 | 0.31391 | 0.55294 | 5.4735 | 4.8144 | 0.85882 | 0.48306 | 0.7441 | 1.0132 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 51.0413 | 0.18375 | 41.4144 | 0.14909 | 8.9564 | 0.032243 | 0.11337 | 9.5038 | 0.034214 | 0.1203 | 0.078856 | 0.069361 | 283.8822 | 249.6982 | 0.0082404 | 0.004635 | 29.6656 | 16.6858 | 0.016492 | 0.014842 | 59.372 | 53.4318 | 8.5475 | 8.6325 | 3.074 | 3.6633 | 1.4569 | 1.4003 | 0.65562 | 0.9172 | 0.73837 | 0.99995 | 0.304 | 0.53548 | 19.2134 | 3074.0001 | 3818.1537 | 0.8608 | 1.1657 | 99.5797 | 175.4035 | 0.28795 | 0.35766 | 0.21657 | 0.2933 | 0.72026 | 1.0049 | 0.27165 | 0.33742 | 0.43291 | 0.65502 | 0.53551 | 0.41172 | 0.14909 | 0.1203 | 372.9197 | 319.8158
2013-03-05 | 42 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 27996.3014 | 19 | 75147.2537 | 17 | 2 | 5 | 386.9335 | 81.0536 | 180 | 3.1963 | 17 | 1250 | 85943.8755 | 11744.9925 | 371.4364 | 10.0747 | 13.0025 | 37 | 29.8943 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 7.1057 | 180 | 2.9278 | 12.6921 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0753 | 484.516 | 1165.5813 |  | 681.0653 | 11041.8883 | 3131.1356 | 1166.5126 | 0.23048 | 21.8492 | 22.5149 | 0.02 | 0.05 | 30 | 165 | 453 | 659.9335 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 526.5214 | 26.0509 | 1.1207 | 1.0176 | 208.0653 | 473 | 438 | 446.9491 | 212.9844 | 0.2189 | 0.027 | 1.06 | 12.2194 | 12.2194 | 659.9335 | 681.0653 | 1.1207 | 1.1264 | 2.6917 | 2.9595 | 659.9335 | 681.0653 | 12.8075 | 1.1207 | 1.1264 | 298.15 | 1.7927 | 1.971 | 659.9335 | 6.423 | 1.1207 | 298.15 | 0.89903 | 0.98848 | 3.1311 | 4.178 | 22.5149 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.084811 | 0.084811 | 12.8075 | 435 | 446.9491 | 1.0625 | 1.0661 | 298.15 | 0.32963 | 0.38361 | 0.88786 | 453 | 2816.5993 | 6.5855 | 0.76158 | 1.1152 | 21.47 | 125.1952 | 0.42344 | 0.077255 | 0.077255 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 104.0022 | 42.2483 | 0.14706 | 0.31739 | 0.75299 | 104.0022 | 54.5013 | 0.18789 | 0.32579 | 0.77291 | 6.3966 | 5.0819 | 0.78628 | 0.55709 | 0.76577 | 1.1309 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 54.6203 | 0.19663 | 40.0105 | 0.14404 | 9.5482 | 0.034374 | 0.12086 | 10.3336 | 0.037201 | 0.1308 | 0.092156 | 0.073214 | 331.7602 | 263.572 | 0.0075444 | 0.0053453 | 27.16 | 19.243 | 0.015884 | 0.016718 | 57.1832 | 60.1834 | 9.5277 | 9.2599 | 3.1311 | 4.6596 | 1.4091 | 1.5874 | 0.67677 | 1.0304 | 0.76158 | 1.1152 | 0.31739 | 0.75299 | 19.2305 | 3131.1356 | 4178.0355 | 0.88786 | 1.3001 | 104.0022 | 246.7388 | 0.27162 | 0.36243 | 0.20689 | 0.30295 | 0.71214 | 0.6731 | 0.25624 | 0.34192 | 0.46257 | 0.64907 | 0.67523 | 0.41675 | 0.14404 | 0.1308 | 416.1034 | 342.9983
2013-03-06 | 43 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 33063.2765 | 19 | 71674.3314 | 17 | 2 | 5 | 396.572 | 82.2587 | 180 | 3.2694 | 17 | 1250 | 85680.4485 | 11918.9655 | 352.8941 | 10.2494 | 13.8183 | 37 | 30.4199 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 6.5801 | 180 | 3.5689 | 12.7196 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0847 | 522.0345 | 1255.8382 |  | 733.8037 | 11922.7248 | 2986.4305 | 1377.6365 | 0.2722 | 20.7585 | 22.8496 | 0.02 | 0.05 | 30 | 165 | 453 | 669.572 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 538.5577 | 26.5888 | 1.1233 | 1.0194 | 260.8037 | 473 | 438 | 446.4112 | 223.1607 | 0.2189 | 0.027 | 1.06 | 14.431 | 14.431 | 669.572 | 733.8037 | 1.1233 | 1.1407 | 2.8189 | 3.6739 | 669.572 | 733.8037 | 12.8353 | 1.1233 | 1.1407 | 298.15 | 1.8774 | 2.4468 | 669.572 | 6.4369 | 1.1233 | 298.15 | 0.9415 | 1.2271 | 2.9864 | 5.0589 | 22.8496 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.086072 | 0.086072 | 12.8353 | 435 | 446.4112 | 1.0625 | 1.066 | 298.15 | 0.33035 | 0.38195 | 0.90816 | 453 | 2816.5993 | 6.5855 | 0.77899 | 1.4041 | 21.47 | 127.3952 | 0.43077 | 0.077567 | 0.077567 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 98.8103 | 42.9792 | 0.1495 | 0.30202 | 0.8225 | 98.8103 | 57.9155 | 0.19927 | 0.31175 | 0.84898 | 8.6257 | 5.6982 | 0.85408 | 0.74688 | 0.78482 | 1.4267 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 67.3225 | 0.24236 | 37.3076 | 0.13431 | 10.8201 | 0.038952 | 0.13696 | 11.9014 | 0.042845 | 0.15065 | 0.12427 | 0.082094 | 447.3745 | 295.5374 | 0.008195 | 0.0071663 | 29.5019 | 25.7988 | 0.016812 | 0.021446 | 60.5241 | 77.2063 | 11.6121 | 10.7571 | 2.9864 | 6.5259 | 1.4954 | 2.0649 | 0.69292 | 1.318 | 0.77899 | 1.4041 | 0.30202 | 0.8225 | 19.2722 | 2986.4305 | 5058.8719 | 0.90816 | 1.6369 | 98.8103 | 269.0919 | 0.21936 | 0.37159 | 0.17924 | 0.32306 | 0.72491 | 1.1419 | 0.20695 | 0.35056 | 0.44791 | 0.6383 | 0.58579 | 0.38771 | 0.13431 | 0.15065 | 537.4004 | 398.5425
2013-03-07 | 44 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 32956.0057 | 19 | 72339.1264 | 17 | 2 | 5 | 401.6336 | 83.0151 | 180 | 3.2814 | 17 | 1250 | 87506.1735 | 12120.4373 | 359.8119 | 10.687 | 14.2459 | 37 | 30.6227 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 6.3773 | 180 | 3.5589 | 12.7191 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0845 | 521.2419 | 1253.9315 |  | 732.6896 | 11904.077 | 3014.1303 | 1373.1669 | 0.27131 | 21.1654 | 23.0597 | 0.02 | 0.05 | 30 | 165 | 453 | 674.6336 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 540.5352 | 26.6876 | 1.1247 | 1.0203 | 259.6896 | 473 | 438 | 446.3124 | 228.3213 | 0.2189 | 0.027 | 1.06 | 14.3842 | 14.3842 | 674.6336 | 732.6896 | 1.1247 | 1.1404 | 2.8832 | 3.6583 | 674.6336 | 732.6896 | 12.8347 | 1.1247 | 1.1404 | 298.15 | 1.9202 | 2.4364 | 674.6336 | 6.4366 | 1.1247 | 298.15 | 0.96298 | 1.2219 | 3.0141 | 5.0402 | 23.0597 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.086863 | 0.086863 | 12.8347 | 435 | 446.3124 | 1.0625 | 1.066 | 298.15 | 0.33034 | 0.38147 | 0.91149 | 453 | 2816.5993 | 6.5855 | 0.78185 | 1.3997 | 21.47 | 128.2438 | 0.43359 | 0.077687 | 0.077687 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 100.7473 | 44.8107 | 0.1556 | 0.30916 | 0.82888 | 100.7473 | 59.7049 | 0.20523 | 0.31905 | 0.85539 | 8.4869 | 5.6857 | 0.89487 | 0.74208 | 0.78796 | 1.4225 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 66.1725 | 0.23822 | 37.3566 | 0.13448 | 10.8374 | 0.039015 | 0.13718 | 11.8735 | 0.042745 | 0.1503 | 0.12227 | 0.081914 | 440.1733 | 294.8888 | 0.0085863 | 0.0071203 | 30.9106 | 25.6331 | 0.017296 | 0.021363 | 62.2639 | 76.9076 | 11.501 | 10.7259 | 3.0141 | 6.3661 | 1.5387 | 2.0549 | 0.69499 | 1.3129 | 0.78185 | 1.3997 | 0.30916 | 0.82888 | 19.2713 | 3014.1303 | 5040.2241 | 0.91149 | 1.6318 | 100.7473 | 270.1132 | 0.22212 | 0.37142 | 0.18048 | 0.3231 | 0.72178 | 1.218 | 0.20954 | 0.3504 | 0.43714 | 0.63888 | 0.59218 | 0.39542 | 0.13448 | 0.1503 | 533.3478 | 397.4295
2013-03-08 | 45 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 32258.5318 | 19 | 69409.6075 | 17 | 2 | 5 | 406.0629 | 95.2009 | 180 | 3.856 | 17 | 1250 | 89160.1529 | 12574.7318 | 373.8387 | 10.5057 | 14.6131 | 37 | 30.5848 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 6.4152 | 180 | 4.1074 | 12.7153 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0832 | 516.0866 | 1241.5296 |  | 725.443 | 11782.829 | 2892.067 | 1344.1055 | 0.26557 | 21.9905 | 26.4447 | 0.02 | 0.05 | 30 | 165 | 453 | 679.0629 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 635.1857 | 31.3701 | 1.1259 | 1.0219 | 252.443 | 473 | 438 | 441.6299 | 237.433 | 0.2189 | 0.027 | 1.06 | 14.0798 | 14.0798 | 679.0629 | 725.443 | 1.1259 | 1.1384 | 2.9391 | 3.557 | 679.0629 | 725.443 | 12.8309 | 1.1259 | 1.1384 | 298.15 | 1.9575 | 2.3689 | 679.0629 | 6.4347 | 1.1259 | 298.15 | 0.98167 | 1.188 | 2.8921 | 4.919 | 26.4447 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.099614 | 0.099614 | 12.8309 | 435 | 441.6299 | 1.0628 | 1.0649 | 298.15 | 0.33035 | 0.35995 | 1.0711 | 453 | 2816.5993 | 6.5855 | 0.91876 | 1.3617 | 21.47 | 128.0854 | 0.43307 | 0.077664 | 0.077664 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 104.6748 | 44.0521 | 0.15307 | 0.32069 | 0.69416 | 104.6748 | 61.242 | 0.21035 | 0.33254 | 0.71982 | 8.2486 | 5.6038 | 0.80796 | 0.74691 | 0.92682 | 1.3836 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 67.1702 | 0.24181 | 37.6825 | 0.13566 | 10.7167 | 0.03858 | 0.13565 | 11.5563 | 0.041603 | 0.14628 | 0.11884 | 0.080734 | 427.8134 | 290.6427 | 0.0077525 | 0.0071666 | 27.9089 | 25.7999 | 0.017664 | 0.021132 | 63.5916 | 76.0745 | 11.1406 | 10.5228 | 2.8921 | 5.9779 | 1.5975 | 2.009 | 0.81915 | 1.2621 | 0.91876 | 1.3617 | 0.32069 | 0.69416 | 19.2656 | 2892.067 | 4918.9761 | 1.0711 | 1.5875 | 104.6748 | 226.5786 | 0.21773 | 0.37033 | 0.21666 | 0.32111 | 0.73494 | 1.7164 | 0.20541 | 0.34937 | 0.50344 | 0.62822 | 0.50977 | 0.34904 | 0.13566 | 0.14628 | 519.3139 | 392.5172
2013-03-09 | 46 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 28585.5457 | 19 | 68541.1028 | 17 | 2 | 5 | 399.7557 | 85.9824 | 180 | 3.4438 | 17 | 1250 | 80084.291 | 10722.0471 | 352.9254 | 9.8317 | 12.9227 | 37 | 29.9284 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 7.0716 | 180 | 3.091 | 12.6953 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0764 | 488.8874 | 1176.0975 |  | 687.2101 | 11144.3218 | 2855.8793 | 1191.0644 | 0.23533 | 20.7603 | 23.884 | 0.02 | 0.05 | 30 | 165 | 453 | 672.7557 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 567.2945 | 28.0612 | 1.1242 | 1.0202 | 214.2101 | 473 | 438 | 444.9388 | 227.8169 | 0.2189 | 0.027 | 1.06 | 12.4766 | 12.4766 | 672.7557 | 687.2101 | 1.1242 | 1.1281 | 2.8539 | 3.0399 | 672.7557 | 687.2101 | 12.8107 | 1.1242 | 1.1281 | 298.15 | 1.9007 | 2.0245 | 672.7557 | 6.4246 | 1.1242 | 298.15 | 0.95319 | 1.0153 | 2.8559 | 4.2805 | 23.884 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.089968 | 0.089968 | 12.8107 | 435 | 444.9388 | 1.0626 | 1.0657 | 298.15 | 0.32975 | 0.37444 | 0.95661 | 453 | 2816.5993 | 6.5855 | 0.82056 | 1.1519 | 21.47 | 125.3382 | 0.42391 | 0.077276 | 0.077276 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 98.8191 | 41.2312 | 0.14368 | 0.30091 | 0.74078 | 98.8191 | 54.1675 | 0.18678 | 0.30933 | 0.76152 | 6.7669 | 5.1563 | 0.84033 | 0.58816 | 0.8248 | 1.1685 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 60.3642 | 0.21731 | 39.6483 | 0.14273 | 9.6483 | 0.034734 | 0.12213 | 10.5005 | 0.037802 | 0.13292 | 0.09749 | 0.074287 | 350.9654 | 267.4324 | 0.008063 | 0.0056434 | 29.0268 | 20.3163 | 0.017017 | 0.017421 | 61.2599 | 62.7154 | 9.6228 | 9.4368 | 2.8559 | 4.61 | 1.5262 | 1.6501 | 0.73059 | 1.0619 | 0.82056 | 1.1519 | 0.30091 | 0.74078 | 19.2353 | 2855.8793 | 4280.469 | 0.95661 | 1.3429 | 98.8191 | 243.272 | 0.24263 | 0.36366 | 0.21832 | 0.30649 | 0.69768 | 0.74602 | 0.2289 | 0.34308 | 0.46507 | 0.64356 | 0.64309 | 0.36671 | 0.14273 | 0.13292 | 441.2521 | 350.464
2013-03-10 | 47 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 27012.8326 | 19 | 77616.3631 | 17 | 2 | 5 | 377.6022 | 77.1005 | 180 | 3.1368 | 17 | 1250 | 38673.3329 | 4788.6716 | 167.4424 | 10.9748 | 13.9054 | 37 | 29.1782 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 7.8218 | 180 | 2.9306 | 12.6868 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0735 | 477.215 | 1148.0176 |  | 670.8026 | 10870.9234 | 3234.0151 | 1125.5347 | 0.22239 | 9.8496 | 21.4168 | 0.02 | 0.05 | 30 | 165 | 453 | 650.6022 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 516.7135 | 25.5764 | 1.1183 | 1.016 | 197.8026 | 473 | 438 | 447.4236 | 203.1786 | 0.2189 | 0.027 | 1.06 | 11.7902 | 11.7902 | 650.6022 | 670.8026 | 1.1183 | 1.1237 | 2.5753 | 2.8271 | 650.6022 | 670.8026 | 12.8021 | 1.1183 | 1.1237 | 298.15 | 1.7151 | 1.8829 | 650.6022 | 6.4203 | 1.1183 | 298.15 | 0.86014 | 0.94427 | 3.234 | 4.0071 | 21.4168 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.080675 | 0.080675 | 12.8021 | 435 | 447.4236 | 1.0624 | 1.0663 | 298.15 | 0.32948 | 0.38565 | 0.87132 | 453 | 2816.5993 | 6.5855 | 0.7474 | 1.0574 | 21.47 | 122.1984 | 0.41345 | 0.076831 | 0.076831 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 46.8839 | 46.0152 | 0.15962 | 0.14424 | 0.69463 | 46.8839 | 58.2799 | 0.20048 | 0.14803 | 0.71287 | 5.9809 | 4.956 | 0.71893 | 0.52056 | 0.74655 | 1.071 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 51.4893 | 0.18536 | 40.6502 | 0.14634 | 7.7144 | 0.027772 | 0.097651 | 9.9947 | 0.035981 | 0.12652 | 0.086167 | 0.071401 | 310.2007 | 257.0421 | 0.0068982 | 0.0049948 | 24.8334 | 17.9812 | 0.014887 | 0.015753 | 53.5946 | 56.7106 | 9.2149 | 8.963 | 3.234 | 4.4672 | 1.3295 | 1.4972 | 0.66672 | 0.97668 | 0.7474 | 1.0574 | 0.14424 | 0.69463 | 19.2224 | 3234.0151 | 4007.0705 | 0.87132 | 1.2327 | 46.8839 | 225.7786 | 0.29076 | 0.36026 | 0.21042 | 0.29768 | 0.64525 | 0.57311 | 0.2743 | 0.33986 | 0.48116 | 0.65232 | 0.65695 | 0.19299 | 0.14634 | 0.12652 | 388.6287 | 331.7339
2013-03-11 | 48 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 27189.6094 | 19 | 78793.495 | 17 | 2 | 5 | 403.6243 | 88.3019 | 180 | 3.4574 | 17 | 1250 | 89499.5504 | 11879.0701 | 355.8571 | 11.9579 | 15.6046 | 37 | 31.4979 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 5.5021 | 180 | 3.6467 | 12.6877 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0738 | 478.5278 | 1151.1757 |  | 672.6479 | 10901.654 | 3283.0623 | 1132.9004 | 0.22384 | 20.9328 | 24.5283 | 0.02 | 0.05 | 30 | 165 | 453 | 676.6243 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 569.5403 | 28.1891 | 1.1252 | 1.0209 | 199.6479 | 473 | 438 | 444.8109 | 231.8134 | 0.2189 | 0.027 | 1.06 | 11.8673 | 11.8673 | 676.6243 | 672.6479 | 1.1252 | 1.1242 | 2.9015 | 2.8508 | 676.6243 | 672.6479 | 12.8031 | 1.1252 | 1.1242 | 298.15 | 1.9324 | 1.8986 | 676.6243 | 6.4208 | 1.1252 | 298.15 | 0.9691 | 0.95216 | 3.2831 | 4.0378 | 24.5283 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.092395 | 0.092395 | 12.8031 | 435 | 444.8109 | 1.0626 | 1.0656 | 298.15 | 0.32956 | 0.37363 | 0.9604 | 453 | 2816.5993 | 6.5855 | 0.82381 | 1.074 | 21.47 | 131.9067 | 0.4458 | 0.078205 | 0.078205 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 99.64 | 50.1294 | 0.17332 | 0.30925 | 0.61661 | 99.64 | 65.3914 | 0.22418 | 0.31927 | 0.63659 | 5.6828 | 4.9788 | 0.87143 | 0.54343 | 0.83057 | 1.0907 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 49.627 | 0.17866 | 40.5318 | 0.14591 | 9.3254 | 0.033571 | 0.11804 | 9.9734 | 0.035904 | 0.12625 | 0.081872 | 0.071729 | 294.7385 | 258.2239 | 0.0083614 | 0.0052143 | 30.101 | 18.7714 | 0.017464 | 0.016259 | 62.8715 | 58.5326 | 8.9658 | 9.0166 | 3.2831 | 3.9472 | 1.5588 | 1.525 | 0.73141 | 0.98156 | 0.82381 | 1.074 | 0.30925 | 0.61661 | 19.2238 | 3283.0623 | 4037.8012 | 0.9604 | 1.252 | 99.64 | 198.6688 | 0.29325 | 0.36066 | 0.23042 | 0.30039 | 0.69165 | 1.9054 | 0.27665 | 0.34024 | 0.45632 | 0.64365 | 0.57415 | 0.37539 | 0.14591 | 0.12625 | 387.711 | 335.5279
2013-03-12 | 49 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 25934.8242 | 19 | 68890.3556 | 17 | 2 | 5 | 389.1665 | 145.2064 | 180 | 6.1267 | 17 | 1250 | 87161.2611 | 12232.1668 | 371.8321 | 10.0805 | 13.6996 | 37 | 29.154 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 7.846 | 180 | 3.619 | 12.6809 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0715 | 469.2051 | 1128.7485 |  | 659.5434 | 10683.5238 | 2870.4315 | 1080.6177 | 0.21351 | 21.8725 | 40.3351 | 0.02 | 0.05 | 30 | 165 | 453 | 662.1665 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 1009.236 | 49.9785 | 1.1213 | 1.0222 | 186.5434 | 473 | 438 | 423.0215 | 239.145 | 0.2189 | 0.027 | 1.06 | 11.3197 | 11.3197 | 662.1665 | 659.5434 | 1.1213 | 1.1206 | 2.7172 | 2.6845 | 662.1665 | 659.5434 | 12.7962 | 1.1213 | 1.1206 | 298.15 | 1.8096 | 1.7879 | 662.1665 | 6.4173 | 1.1213 | 298.15 | 0.90754 | 0.89662 | 2.8704 | 3.8197 | 40.3351 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.15194 | 0.15194 | 12.7962 | 435 | 423.0215 | 1.0641 | 1.0605 | 298.15 | 0.32985 | 0.27915 | 1.7018 | 453 | 2816.5993 | 6.5855 | 1.4598 | 0.99947 | 21.47 | 122.0973 | 0.41311 | 0.076817 | 0.076817 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 104.113 | 42.2725 | 0.14714 | 0.31775 | 0.51924 | 104.113 | 57.4186 | 0.19761 | 0.32814 | 0.53622 | 5.7321 | 4.8155 | 0.17193 | 0.66119 | 1.4655 | 1.0118 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 54.9373 | 0.19777 | 41.408 | 0.14907 | 9.0083 | 0.03243 | 0.11403 | 9.4834 | 0.03414 | 0.12004 | 0.082582 | 0.069377 | 297.2941 | 249.7577 | 0.0016497 | 0.0063441 | 5.9389 | 22.8389 | 0.015911 | 0.017282 | 57.2781 | 62.2154 | 8.6025 | 8.6352 | 2.8704 | 3.7599 | 1.5305 | 1.5087 | 1.3079 | 0.84753 | 1.4598 | 0.99947 | 0.31775 | 0.51924 | 19.2135 | 2870.4315 | 3819.6709 | 1.7018 | 1.1652 | 104.113 | 170.1338 | 0.26879 | 0.35768 | 0.42803 | 0.29306 | 0.73132 | 0.81887 | 0.25358 | 0.33744 | 0.88381 | 0.56175 | 0.51951 | 0.21766 | 0.14907 | 0.12004 | 360.5111 | 334.812
2013-03-13 | 50 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 28007.8521 | 19 | 82461.2908 | 17 | 2 | 5 | 395.261 | 120.4205 | 180 | 4.8649 | 17 | 1250 | 88678.7378 | 12282.7094 | 357.77 | 10.7806 | 14.799 | 37 | 28.8616 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 8.1384 | 180 | 4.0184 | 12.6922 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0753 | 484.6017 | 1165.7875 |  | 681.1858 | 11043.8963 | 3435.8871 | 1166.9938 | 0.23058 | 21.0453 | 33.4501 | 0.02 | 0.05 | 30 | 165 | 453 | 668.261 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 801.3912 | 39.6506 | 1.123 | 1.0214 | 208.1858 | 473 | 438 | 433.3494 | 234.9116 | 0.2189 | 0.027 | 1.06 | 12.2245 | 12.2245 | 668.261 | 681.1858 | 1.123 | 1.1265 | 2.7962 | 2.9611 | 668.261 | 681.1858 | 12.8076 | 1.123 | 1.1265 | 298.15 | 1.8623 | 1.9721 | 668.261 | 6.423 | 1.123 | 298.15 | 0.93393 | 0.98901 | 3.4359 | 4.18 | 33.4501 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.126 | 0.126 | 12.8076 | 435 | 433.3494 | 1.0634 | 1.0629 | 298.15 | 0.32993 | 0.32273 | 1.3514 | 453 | 2816.5993 | 6.5855 | 1.1592 | 1.118 | 21.47 | 120.8736 | 0.40904 | 0.076644 | 0.076644 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 100.1756 | 45.2025 | 0.15691 | 0.30766 | 0.5369 | 100.1756 | 62.0198 | 0.21294 | 0.31876 | 0.55627 | 5.9924 | 5.0833 | 0.49917 | 0.65732 | 1.1654 | 1.1326 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 49.3587 | 0.17769 | 40.0032 | 0.14401 | 9.5211 | 0.034276 | 0.12052 | 10.1155 | 0.036416 | 0.12804 | 0.086332 | 0.073236 | 310.797 | 263.6481 | 0.0047896 | 0.0063071 | 17.2425 | 22.7054 | 0.016585 | 0.018068 | 59.7074 | 65.0447 | 9.4283 | 9.2634 | 3.4359 | 4.4746 | 1.5395 | 1.6494 | 1.0332 | 0.99204 | 1.1592 | 1.118 | 0.30766 | 0.5369 | 19.2306 | 3435.8871 | 4180.0434 | 1.3514 | 1.3034 | 100.1756 | 174.8165 | 0.29793 | 0.36246 | 0.31477 | 0.3036 | 0.72177 | 0.93124 | 0.28107 | 0.34194 | 0.67424 | 0.60147 | 0.48022 | 0.26542 | 0.14401 | 0.12804 | 387.7468 | 351.3982
2013-03-14 | 51 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 27200.1873 | 19 | 78428.5467 | 17 | 2 | 5 | 391.1656 | 98.5846 | 180 | 3.9215 | 17 | 1250 | 88727.8275 | 12492.446 | 370.6045 | 9.5196 | 13.4514 | 37 | 28.7518 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 8.2482 | 180 | 3.9318 | 12.6878 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0738 | 478.6063 | 1151.3647 |  | 672.7583 | 10903.4929 | 3267.8561 | 1133.3411 | 0.22393 | 21.8003 | 27.3846 | 0.02 | 0.05 | 30 | 165 | 453 | 664.1656 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 645.9773 | 31.9722 | 1.1219 | 1.0194 | 199.7583 | 473 | 438 | 441.0278 | 223.1378 | 0.2189 | 0.027 | 1.06 | 11.872 | 11.872 | 664.1656 | 672.7583 | 1.1219 | 1.1242 | 2.7437 | 2.8522 | 664.1656 | 672.7583 | 12.8031 | 1.1219 | 1.1242 | 298.15 | 1.8273 | 1.8996 | 664.1656 | 6.4208 | 1.1219 | 298.15 | 0.91639 | 0.95264 | 3.2679 | 4.0396 | 27.3846 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.10315 | 0.10315 | 12.8031 | 435 | 441.0278 | 1.0629 | 1.0647 | 298.15 | 0.32965 | 0.35646 | 1.0893 | 453 | 2816.5993 | 6.5855 | 0.93437 | 1.0714 | 21.47 | 120.4141 | 0.40751 | 0.076579 | 0.076579 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 103.7692 | 39.925 | 0.13932 | 0.31509 | 0.51241 | 103.7692 | 56.3799 | 0.19415 | 0.32634 | 0.53071 | 5.8604 | 4.9801 | 0.66644 | 0.5749 | 0.94074 | 1.0848 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 50.574 | 0.18207 | 40.5247 | 0.14589 | 9.3345 | 0.033604 | 0.11816 | 9.8427 | 0.035434 | 0.12459 | 0.084431 | 0.071748 | 303.9515 | 258.2945 | 0.0063945 | 0.0055162 | 23.0202 | 19.8585 | 0.016263 | 0.016589 | 58.5485 | 59.7198 | 9.1283 | 9.0198 | 3.2679 | 4.2354 | 1.4708 | 1.5431 | 0.83121 | 0.96821 | 0.93437 | 1.0714 | 0.31509 | 0.51241 | 19.2239 | 3267.8561 | 4039.64 | 1.0893 | 1.249 | 103.7692 | 168.7522 | 0.29177 | 0.36068 | 0.26125 | 0.29955 | 0.73369 | 0.86916 | 0.27526 | 0.34027 | 0.55501 | 0.62744 | 0.47828 | 0.33722 | 0.14589 | 0.12459 | 385.5202 | 337.8728
2013-03-15 | 52 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 25746.5328 | 19 | 67878.8842 | 17 | 2 | 5 | 387.9328 | 87.7024 | 180 | 3.4399 | 17 | 1250 | 81600.8305 | 11760.1623 | 352.3146 | 9.99 | 13.7114 | 37 | 28.4461 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 8.5539 | 180 | 3.7214 | 12.6799 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0712 | 467.8053 | 1125.381 |  | 657.5757 | 10650.7914 | 2828.2868 | 1072.7722 | 0.21196 | 20.7244 | 24.3618 | 0.02 | 0.05 | 30 | 165 | 453 | 660.9328 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 566.6493 | 28.0634 | 1.121 | 1.0182 | 184.5757 | 473 | 438 | 444.9366 | 215.9962 | 0.2189 | 0.027 | 1.06 | 11.2375 | 11.2375 | 660.9328 | 657.5757 | 1.121 | 1.1201 | 2.7016 | 2.6598 | 660.9328 | 657.5757 | 12.7952 | 1.121 | 1.1201 | 298.15 | 1.7992 | 1.7714 | 660.9328 | 6.4168 | 1.121 | 298.15 | 0.90232 | 0.88838 | 2.8283 | 3.7869 | 24.3618 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.091768 | 0.091768 | 12.7952 | 435 | 444.9366 | 1.0626 | 1.0657 | 298.15 | 0.32935 | 0.37397 | 0.95553 | 453 | 2816.5993 | 6.5855 | 0.81963 | 0.98855 | 21.47 | 119.1347 | 0.40324 | 0.076398 | 0.076398 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 98.6481 | 41.8936 | 0.14588 | 0.30082 | 0.48507 | 98.6481 | 57.4682 | 0.19778 | 0.31094 | 0.50139 | 5.7076 | 4.7907 | 0.74203 | 0.50069 | 0.82468 | 0.99981 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 55.4168 | 0.1995 | 41.547 | 0.14957 | 8.888 | 0.031997 | 0.11251 | 9.3755 | 0.033752 | 0.11868 | 0.08223 | 0.06902 | 296.0274 | 248.4716 | 0.0071199 | 0.0048041 | 25.6315 | 17.2949 | 0.01598 | 0.014949 | 57.5277 | 53.8175 | 8.5359 | 8.5777 | 2.8283 | 3.7105 | 1.4253 | 1.3975 | 0.72786 | 0.89678 | 0.81963 | 0.98855 | 0.30082 | 0.48507 | 19.212 | 2828.2868 | 3786.9386 | 0.95553 | 1.1525 | 98.6481 | 159.068 | 0.26678 | 0.35721 | 0.24208 | 0.29197 | 0.75101 | 0.7335 | 0.25168 | 0.33699 | 0.49518 | 0.64172 | 0.49068 | 0.36702 | 0.14957 | 0.11868 | 379.1866 | 319.584
2013-03-18 | 54 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 28337.7758 | 19 | 76271.3092 | 17 | 2 | 5 | 398.8689 | 92.8142 | 180 | 3.6646 | 17 | 1250 | 85945.6247 | 11910.2878 | 351.5907 | 11.252 | 15.3827 | 37 | 29.5969 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 7.4031 | 180 | 4.1307 | 12.694 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0759 | 487.0495 | 1171.6762 |  | 684.6267 | 11101.2498 | 3177.9712 | 1180.7407 | 0.23329 | 20.6818 | 25.7817 | 0.02 | 0.05 | 30 | 165 | 453 | 671.8689 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 603.6689 | 29.8636 | 1.124 | 1.0203 | 211.6267 | 473 | 438 | 443.1364 | 228.7325 | 0.2189 | 0.027 | 1.06 | 12.3685 | 12.3685 | 671.8689 | 684.6267 | 1.124 | 1.1274 | 2.8423 | 3.006 | 671.8689 | 684.6267 | 12.8094 | 1.124 | 1.1274 | 298.15 | 1.893 | 2.002 | 671.8689 | 6.4239 | 1.124 | 298.15 | 0.94932 | 1.004 | 3.178 | 4.2374 | 25.7817 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.097117 | 0.097117 | 12.8094 | 435 | 443.1364 | 1.0627 | 1.0652 | 298.15 | 0.32976 | 0.36617 | 1.018 | 453 | 2816.5993 | 6.5855 | 0.87317 | 1.1377 | 21.47 | 123.9507 | 0.41929 | 0.077079 | 0.077079 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 98.4454 | 47.1752 | 0.16348 | 0.30363 | 0.54779 | 98.4454 | 64.4627 | 0.22108 | 0.31484 | 0.56802 | 6.3482 | 5.1251 | 0.78715 | 0.59528 | 0.88 | 1.1535 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 53.8084 | 0.19371 | 39.7987 | 0.14328 | 9.5948 | 0.034541 | 0.12145 | 10.2277 | 0.03682 | 0.12946 | 0.091459 | 0.073837 | 329.2516 | 265.8138 | 0.0075527 | 0.0057117 | 27.1899 | 20.5622 | 0.017008 | 0.0174 | 61.229 | 62.6392 | 9.5262 | 9.3625 | 3.178 | 4.5282 | 1.5268 | 1.6358 | 0.77606 | 1.0405 | 0.87317 | 1.1377 | 0.30363 | 0.54779 | 19.2333 | 3177.9712 | 4237.3969 | 1.018 | 1.3263 | 98.4454 | 177.6105 | 0.27236 | 0.36315 | 0.23435 | 0.30534 | 0.72214 | 1.2104 | 0.25694 | 0.3426 | 0.49645 | 0.6361 | 0.48151 | 0.34773 | 0.14328 | 0.12946 | 417.6704 | 349.0153
2013-03-19 | 55 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 26377.8889 | 19 | 70937.9169 | 17 | 2 | 5 | 392.5478 | 84.3086 | 180 | 3.3518 | 17 | 1250 | 86389.6075 | 12058.7116 | 368.4892 | 10.519 | 14.3515 | 37 | 29.5744 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 7.4256 | 180 | 3.8325 | 12.6833 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0723 | 472.4981 | 1136.6703 |  | 664.1722 | 10760.5456 | 2955.7465 | 1099.0787 | 0.21716 | 21.6758 | 23.4191 | 0.02 | 0.05 | 30 | 165 | 453 | 665.5478 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 552.1429 | 27.3375 | 1.1223 | 1.0188 | 191.1722 | 473 | 438 | 445.6625 | 219.8853 | 0.2189 | 0.027 | 1.06 | 11.5131 | 11.5131 | 665.5478 | 664.1722 | 1.1223 | 1.1219 | 2.7601 | 2.7428 | 665.5478 | 664.1722 | 12.7986 | 1.1223 | 1.1219 | 298.15 | 1.8382 | 1.8267 | 665.5478 | 6.4185 | 1.1223 | 298.15 | 0.92186 | 0.9161 | 2.9557 | 3.8967 | 23.4191 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.088217 | 0.088217 | 12.7986 | 435 | 445.6625 | 1.0625 | 1.0658 | 298.15 | 0.32943 | 0.37741 | 0.93106 | 453 | 2816.5993 | 6.5855 | 0.79864 | 1.0253 | 21.47 | 123.8564 | 0.41898 | 0.077066 | 0.077066 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 103.177 | 44.1078 | 0.15326 | 0.31614 | 0.51568 | 103.177 | 60.147 | 0.2067 | 0.32704 | 0.53347 | 5.7972 | 4.8736 | 0.79835 | 0.51223 | 0.80515 | 1.0387 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 54.0851 | 0.19471 | 41.0889 | 0.14792 | 9.1238 | 0.032846 | 0.11549 | 9.6076 | 0.034587 | 0.12161 | 0.083521 | 0.070213 | 300.6747 | 252.7678 | 0.0076603 | 0.0049149 | 27.577 | 17.6935 | 0.016407 | 0.015414 | 59.0656 | 55.4903 | 8.753 | 8.7702 | 2.9557 | 3.8654 | 1.4608 | 1.4493 | 0.71043 | 0.93707 | 0.79864 | 1.0253 | 0.31614 | 0.51568 | 19.2172 | 2955.7465 | 3896.6927 | 0.93106 | 1.1953 | 103.177 | 168.3015 | 0.27213 | 0.35877 | 0.23025 | 0.29559 | 0.72739 | 1.0226 | 0.25673 | 0.33846 | 0.47086 | 0.64657 | 0.50296 | 0.39584 | 0.14792 | 0.12161 | 387.3173 | 325.9517
2013-03-20 | 56 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 27856.9939 | 19 | 79753.7331 | 17 | 2 | 5 | 397.7029 | 88.6111 | 180 | 3.5228 | 17 | 1250 | 90439.6756 | 12816.5608 | 364.0689 | 11.2183 | 14.9977 | 37 | 29.3519 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 7.6481 | 180 | 3.7794 | 12.6914 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.075 | 483.4822 | 1163.0943 |  | 679.6121 | 11017.6713 | 3323.0722 | 1160.7081 | 0.22933 | 21.4158 | 24.6142 | 0.02 | 0.05 | 30 | 165 | 453 | 670.7029 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 580.3036 | 28.7136 | 1.1236 | 1.0199 | 206.6121 | 473 | 438 | 444.2864 | 226.4165 | 0.2189 | 0.027 | 1.06 | 12.1586 | 12.1586 | 670.7029 | 679.6121 | 1.1236 | 1.126 | 2.8269 | 2.9407 | 670.7029 | 679.6121 | 12.8067 | 1.1236 | 1.126 | 298.15 | 1.8827 | 1.9585 | 670.7029 | 6.4226 | 1.1236 | 298.15 | 0.94419 | 0.98218 | 3.3231 | 4.1538 | 24.6142 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.092719 | 0.092719 | 12.8067 | 435 | 444.2864 | 1.0626 | 1.0655 | 298.15 | 0.32967 | 0.37134 | 0.97855 | 453 | 2816.5993 | 6.5855 | 0.83938 | 1.1102 | 21.47 | 122.9256 | 0.41587 | 0.076934 | 0.076934 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 101.9393 | 47.0344 | 0.16301 | 0.31431 | 0.57665 | 101.9393 | 62.8514 | 0.21571 | 0.32493 | 0.59614 | 6.0087 | 5.0642 | 0.8064 | 0.56969 | 0.84547 | 1.1251 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 50.6158 | 0.18222 | 40.0983 | 0.14435 | 9.5138 | 0.03425 | 0.12043 | 10.1243 | 0.036447 | 0.12816 | 0.086567 | 0.072959 | 311.64 | 262.6537 | 0.0077374 | 0.0054662 | 27.8547 | 19.6785 | 0.016874 | 0.01684 | 60.7456 | 60.6256 | 9.3317 | 9.218 | 3.3231 | 4.3568 | 1.5114 | 1.5871 | 0.74666 | 1.0174 | 0.83938 | 1.1102 | 0.31431 | 0.57665 | 19.2293 | 3323.0722 | 4153.8184 | 0.97855 | 1.2942 | 101.9393 | 187.0229 | 0.28971 | 0.36213 | 0.22916 | 0.30309 | 0.73848 | 0.9354 | 0.27331 | 0.34164 | 0.48077 | 0.64106 | 0.51943 | 0.37446 | 0.14435 | 0.12816 | 400.2403 | 342.9578
2013-03-28 | 58 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 26320.4056 | 19 | 72350.7544 | 17 | 2 | 5 | 388.7399 | 95.6471 | 180 | 3.7664 | 17 | 1250 | 95020.0042 | 13569.0329 | 381.5929 | 10.6923 | 14.52 | 37 | 29.8838 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 7.1162 | 180 | 3.8277 | 12.683 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0722 | 472.0709 | 1135.6427 |  | 663.5718 | 10750.5528 | 3014.6148 | 1096.6836 | 0.21668 | 22.4466 | 26.5686 | 0.02 | 0.05 | 30 | 165 | 453 | 661.7399 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 620.4402 | 30.7198 | 1.1212 | 1.0187 | 190.5718 | 473 | 438 | 442.2802 | 219.4597 | 0.2189 | 0.027 | 1.06 | 11.488 | 11.488 | 661.7399 | 663.5718 | 1.1212 | 1.1217 | 2.7123 | 2.7352 | 661.7399 | 663.5718 | 12.7983 | 1.1212 | 1.1217 | 298.15 | 1.8064 | 1.8217 | 661.7399 | 6.4184 | 1.1212 | 298.15 | 0.90591 | 0.91356 | 3.0146 | 3.8867 | 26.5686 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.10008 | 0.10008 | 12.7983 | 435 | 442.2802 | 1.0628 | 1.065 | 298.15 | 0.32949 | 0.36197 | 1.0462 | 453 | 2816.5993 | 6.5855 | 0.89743 | 1.0211 | 21.47 | 125.1516 | 0.42329 | 0.077249 | 0.077249 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 106.846 | 44.8327 | 0.15568 | 0.32789 | 0.51982 | 106.846 | 60.8521 | 0.20905 | 0.33917 | 0.5377 | 5.761 | 4.866 | 0.67955 | 0.53865 | 0.9045 | 1.0348 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 53.1373 | 0.19129 | 41.1296 | 0.14807 | 9.1482 | 0.032934 | 0.1158 | 9.5969 | 0.034549 | 0.12148 | 0.082999 | 0.070105 | 298.7976 | 252.3786 | 0.0065203 | 0.0051684 | 23.4732 | 18.6062 | 0.016075 | 0.015735 | 57.8707 | 56.6476 | 8.7757 | 8.7527 | 3.0146 | 3.9284 | 1.4444 | 1.4597 | 0.79735 | 0.92103 | 0.89743 | 1.0211 | 0.32789 | 0.51982 | 19.2167 | 3014.6148 | 3886.6999 | 1.0462 | 1.1904 | 106.846 | 169.3903 | 0.27816 | 0.35863 | 0.25929 | 0.29503 | 0.74415 | 1.118 | 0.26242 | 0.33833 | 0.53988 | 0.63098 | 0.50908 | 0.36536 | 0.14807 | 0.12148 | 380.1416 | 327.6324
2013-03-29 | 59 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 25010.2535 | 19 | 62455.0578 | 17 | 2 | 5 | 369.8315 | 90.9275 | 180 | 3.6748 | 17 | 1250 | 92041.2961 | 12924.5276 | 370.7363 | 10.4275 | 14.1468 | 37 | 29.5923 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 7.4077 | 180 | 3.7193 | 12.6759 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0699 | 462.3294 | 1112.2079 |  | 649.8785 | 10522.7976 | 2602.2941 | 1042.0939 | 0.2059 | 21.808 | 25.2576 | 0.02 | 0.05 | 30 | 165 | 453 | 642.8315 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 605.341 | 29.989 | 1.1162 | 1.0155 | 176.8785 | 473 | 438 | 443.011 | 199.8205 | 0.2189 | 0.027 | 1.06 | 10.9161 | 10.9161 | 642.8315 | 649.8785 | 1.1162 | 1.1181 | 2.4785 | 2.5642 | 642.8315 | 649.8785 | 12.7911 | 1.1162 | 1.1181 | 298.15 | 1.6507 | 1.7078 | 642.8315 | 6.4148 | 1.1162 | 298.15 | 0.82782 | 0.85644 | 2.6023 | 3.6589 | 25.2576 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.095142 | 0.095142 | 12.7911 | 435 | 443.011 | 1.0627 | 1.0652 | 298.15 | 0.32929 | 0.36508 | 1.0208 | 453 | 2816.5993 | 6.5855 | 0.87559 | 0.94294 | 21.47 | 123.9314 | 0.41923 | 0.077077 | 0.077077 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 103.8062 | 43.7245 | 0.15198 | 0.3178 | 0.47806 | 103.8062 | 59.2902 | 0.20385 | 0.32845 | 0.49407 | 5.8353 | 4.693 | 0.54094 | 0.49489 | 0.88185 | 0.95457 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 59.6853 | 0.21487 | 42.1116 | 0.1516 | 8.7376 | 0.031455 | 0.1106 | 9.1501 | 0.03294 | 0.11582 | 0.08407 | 0.067612 | 302.6508 | 243.4025 | 0.0051903 | 0.0047485 | 18.6852 | 17.0945 | 0.014326 | 0.014506 | 51.5741 | 52.2201 | 8.4376 | 8.3519 | 2.6023 | 3.8193 | 1.2856 | 1.3427 | 0.78045 | 0.84779 | 0.87559 | 0.94294 | 0.3178 | 0.47806 | 19.2059 | 2602.2941 | 3658.9447 | 1.0208 | 1.0993 | 103.8062 | 156.1522 | 0.25269 | 0.3553 | 0.26621 | 0.28669 | 0.73174 | 0.96688 | 0.23839 | 0.33519 | 0.59063 | 0.63142 | 0.50699 | 0.36296 | 0.1516 | 0.11582 | 372.9101 | 312.7171
2013-03-31 | 61 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 27506.3245 | 19 | 79848.7194 | 17 | 2 | 5 | 379.0633 | 100.109 | 180 | 4.0444 | 17 | 1250 | 59489.1895 | 7748.0046 | 247.8845 | 11.0512 | 14.9776 | 37 | 28.6769 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 8.3231 | 180 | 3.9264 | 12.6895 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0744 | 480.8793 | 1156.8327 |  | 675.9534 | 10956.7114 | 3327.03 | 1146.0969 | 0.22645 | 14.5814 | 27.8081 | 0.02 | 0.05 | 30 | 165 | 453 | 652.0633 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 666.2237 | 32.9699 | 1.1186 | 1.0175 | 202.9534 | 473 | 438 | 440.0301 | 212.0332 | 0.2189 | 0.027 | 1.06 | 12.0056 | 12.0056 | 652.0633 | 675.9534 | 1.1186 | 1.1251 | 2.5938 | 2.8933 | 652.0633 | 675.9534 | 12.8048 | 1.1186 | 1.1251 | 298.15 | 1.7274 | 1.9269 | 652.0633 | 6.4216 | 1.1186 | 298.15 | 0.86631 | 0.96637 | 3.327 | 4.0929 | 27.8081 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.10475 | 0.10475 | 12.8048 | 435 | 440.0301 | 1.063 | 1.0645 | 298.15 | 0.32971 | 0.35203 | 1.1234 | 453 | 2816.5993 | 6.5855 | 0.96365 | 1.0855 | 21.47 | 120.1006 | 0.40646 | 0.076535 | 0.076535 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 69.4076 | 46.3349 | 0.16068 | 0.21369 | 0.52768 | 69.4076 | 62.7672 | 0.21543 | 0.2212 | 0.54624 | 6.0848 | 5.0194 | 0.53882 | 0.59417 | 0.96624 | 1.0991 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 50.9024 | 0.18325 | 40.3234 | 0.14516 | 8.766 | 0.031557 | 0.11096 | 9.9552 | 0.035839 | 0.12602 | 0.087664 | 0.072315 | 315.5891 | 260.3324 | 0.00517 | 0.0057011 | 18.6121 | 20.5241 | 0.015087 | 0.016935 | 54.3142 | 60.9675 | 9.4118 | 9.1123 | 3.327 | 4.6372 | 1.3754 | 1.5749 | 0.85891 | 0.98074 | 0.96365 | 1.0855 | 0.21369 | 0.52768 | 19.2264 | 3327.03 | 4092.8585 | 1.1234 | 1.2655 | 69.4076 | 171.3978 | 0.29375 | 0.36137 | 0.26644 | 0.30013 | 0.6787 | 0.85174 | 0.27712 | 0.34091 | 0.6145 | 0.62273 | 0.48612 | 0.22174 | 0.14516 | 0.12602 | 388.5154 | 341.824
2013-04-01 | 62 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 26871.5199 | 19 | 77700.0047 | 17 | 2 | 5 | 387.5712 | 91.2062 | 180 | 3.5864 | 17 | 1250 | 90042.3236 | 12383.6947 | 350.8074 | 10.6507 | 15.7604 | 37 | 29.9484 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 7.0516 | 180 | 5.1097 | 12.686 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0732 | 476.1654 | 1145.4927 |  | 669.3273 | 10846.3578 | 3237.5002 | 1119.6467 | 0.22122 | 20.6357 | 25.3351 | 0.02 | 0.05 | 30 | 165 | 453 | 660.5712 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 590.7827 | 29.2445 | 1.1209 | 1.0183 | 196.3273 | 473 | 438 | 443.7555 | 216.8157 | 0.2189 | 0.027 | 1.06 | 11.7285 | 11.7285 | 660.5712 | 669.3273 | 1.1209 | 1.1233 | 2.6984 | 2.8083 | 660.5712 | 669.3273 | 12.8013 | 1.1209 | 1.1233 | 298.15 | 1.7971 | 1.8703 | 660.5712 | 6.4199 | 1.1209 | 298.15 | 0.90125 | 0.93797 | 3.2375 | 3.9825 | 25.3351 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.095434 | 0.095434 | 12.8013 | 435 | 443.7555 | 1.0627 | 1.0654 | 298.15 | 0.32954 | 0.36876 | 0.99622 | 453 | 2816.5993 | 6.5855 | 0.85453 | 1.0519 | 21.47 | 125.422 | 0.42419 | 0.077287 | 0.077287 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 98.2261 | 44.6587 | 0.1551 | 0.30132 | 0.40459 | 98.2261 | 66.0436 | 0.22635 | 0.31516 | 0.42317 | 5.7926 | 4.9377 | 0.70847 | 0.5451 | 0.8642 | 1.0663 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 50.6116 | 0.1822 | 40.746 | 0.14669 | 9.1838 | 0.033062 | 0.11625 | 9.5376 | 0.034335 | 0.12073 | 0.083455 | 0.071137 | 300.4366 | 256.0948 | 0.0067978 | 0.0052303 | 24.4722 | 18.829 | 0.016031 | 0.016062 | 57.7118 | 57.8242 | 9.0301 | 8.9202 | 3.2375 | 4.182 | 1.4284 | 1.5016 | 0.7591 | 0.95647 | 0.85453 | 1.0519 | 0.30132 | 0.40459 | 19.2212 | 3237.5002 | 3982.5049 | 0.99622 | 1.2263 | 98.2261 | 131.8896 | 0.2926 | 0.35993 | 0.24184 | 0.2977 | 0.71669 | 2.5283 | 0.27604 | 0.33956 | 0.51725 | 0.63698 | 0.38463 | 0.35262 | 0.14669 | 0.12073 | 382.6205 | 332.7481
2013-04-02 | 63 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 26681.2056 | 19 | 77106.9383 | 17 | 2 | 5 | 385.6721 | 76.5542 | 180 | 3.1392 | 17 | 1250 | 92565.714 | 13005.3501 | 368.0347 | 10.9528 | 14.9299 | 37 | 29.5511 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 7.4489 | 180 | 3.9771 | 12.685 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0729 | 474.7517 | 1142.0917 |  | 667.34 | 10813.2738 | 3212.7891 | 1111.7169 | 0.21966 | 21.6491 | 21.2651 | 0.02 | 0.05 | 30 | 165 | 453 | 658.6721 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 517.1237 | 25.6004 | 1.1204 | 1.0174 | 194.34 | 473 | 438 | 447.3996 | 211.2724 | 0.2189 | 0.027 | 1.06 | 11.6454 | 11.6454 | 658.6721 | 667.34 | 1.1204 | 1.1227 | 2.6745 | 2.783 | 658.6721 | 667.34 | 12.8003 | 1.1204 | 1.1227 | 298.15 | 1.7812 | 1.8535 | 658.6721 | 6.4194 | 1.1204 | 298.15 | 0.89329 | 0.92952 | 3.2128 | 3.9494 | 21.2651 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.080103 | 0.080103 | 12.8003 | 435 | 447.3996 | 1.0624 | 1.0663 | 298.15 | 0.32943 | 0.38548 | 0.87201 | 453 | 2816.5993 | 6.5855 | 0.74799 | 1.0407 | 21.47 | 123.759 | 0.41865 | 0.077052 | 0.077052 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 103.0497 | 45.923 | 0.15931 | 0.31698 | 0.50783 | 103.0497 | 62.5676 | 0.21477 | 0.32828 | 0.52594 | 5.7581 | 4.913 | 0.78391 | 0.50739 | 0.75488 | 1.0544 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 50.7353 | 0.18265 | 40.8766 | 0.14716 | 9.1975 | 0.033111 | 0.11642 | 9.6842 | 0.034863 | 0.12258 | 0.082958 | 0.070782 | 298.6473 | 254.8154 | 0.0075216 | 0.0048684 | 27.0778 | 17.5263 | 0.015744 | 0.015461 | 56.6801 | 55.6589 | 8.9709 | 8.8625 | 3.2128 | 4.1468 | 1.3957 | 1.468 | 0.66789 | 0.9606 | 0.74799 | 1.0407 | 0.31698 | 0.50783 | 19.2197 | 3212.7891 | 3949.4209 | 0.87201 | 1.2133 | 103.0497 | 165.0956 | 0.29244 | 0.35949 | 0.2132 | 0.29663 | 0.73214 | 1.0981 | 0.27588 | 0.33914 | 0.46004 | 0.65436 | 0.48797 | 0.42377 | 0.14716 | 0.12258 | 382.4052 | 328.0007
2013-04-03 | 64 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 26719.9736 | 19 | 77787.1983 | 17 | 2 | 5 | 392.6207 | 97.4325 | 180 | 3.9181 | 17 | 1250 | 93125.681 | 13569.1862 | 372.992 | 10.9773 | 15.0488 | 37 | 29.1621 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 7.8379 | 180 | 4.0715 | 12.6852 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0729 | 475.0397 | 1142.7846 |  | 667.7449 | 10820.0131 | 3241.1333 | 1113.3322 | 0.21997 | 21.9407 | 27.0646 | 0.02 | 0.05 | 30 | 165 | 453 | 665.6207 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 645.4283 | 31.9516 | 1.1223 | 1.0196 | 194.7449 | 473 | 438 | 441.0484 | 224.5723 | 0.2189 | 0.027 | 1.06 | 11.6624 | 11.6624 | 665.6207 | 667.7449 | 1.1223 | 1.1228 | 2.7614 | 2.7881 | 665.6207 | 667.7449 | 12.8005 | 1.1223 | 1.1228 | 298.15 | 1.8391 | 1.8569 | 665.6207 | 6.4195 | 1.1223 | 298.15 | 0.92231 | 0.93124 | 3.2411 | 3.9562 | 27.0646 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.10195 | 0.10195 | 12.8005 | 435 | 441.0484 | 1.0629 | 1.0647 | 298.15 | 0.32958 | 0.35648 | 1.0884 | 453 | 2816.5993 | 6.5855 | 0.93358 | 1.0446 | 21.47 | 122.1312 | 0.41323 | 0.076822 | 0.076822 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 104.4378 | 46.0258 | 0.15965 | 0.32132 | 0.49218 | 104.4378 | 63.0654 | 0.21643 | 0.33304 | 0.51014 | 5.6598 | 4.9181 | 0.67788 | 0.55775 | 0.94066 | 1.0579 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 49.9807 | 0.17993 | 40.8499 | 0.14706 | 9.2346 | 0.033245 | 0.11689 | 9.6704 | 0.034813 | 0.12241 | 0.081541 | 0.070855 | 293.5485 | 255.0764 | 0.0065043 | 0.0053516 | 23.4156 | 19.2659 | 0.016383 | 0.016157 | 58.9781 | 58.1653 | 8.901 | 8.8742 | 3.2411 | 4.0045 | 1.4826 | 1.5004 | 0.83163 | 0.94267 | 0.93358 | 1.0446 | 0.32132 | 0.49218 | 19.22 | 3241.1333 | 3956.1603 | 1.0884 | 1.2178 | 104.4378 | 159.9724 | 0.29459 | 0.35958 | 0.26571 | 0.29731 | 0.75929 | 1.0339 | 0.27791 | 0.33922 | 0.55092 | 0.62827 | 0.47116 | 0.34418 | 0.14706 | 0.12241 | 375.9422 | 332.5076
2013-04-04 | 65 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 26959.0309 | 19 | 77877.3447 | 17 | 2 | 5 | 393.3979 | 100.0825 | 180 | 4.0152 | 17 | 1250 | 92096.5599 | 13699.8826 | 383.4079 | 11.7571 | 15.7801 | 37 | 29.612 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 7.388 | 180 | 4.023 | 12.6865 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0734 | 476.8154 | 1147.0563 |  | 670.2409 | 10861.5706 | 3244.8894 | 1123.293 | 0.22194 | 22.5534 | 27.8007 | 0.02 | 0.05 | 30 | 165 | 453 | 666.3979 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 661.4223 | 32.74 | 1.1225 | 1.0199 | 197.2409 | 473 | 438 | 440.26 | 226.1379 | 0.2189 | 0.027 | 1.06 | 11.7667 | 11.7667 | 666.3979 | 670.2409 | 1.1225 | 1.1235 | 2.7715 | 2.82 | 666.3979 | 670.2409 | 12.8018 | 1.1225 | 1.1235 | 298.15 | 1.8458 | 1.8781 | 666.3979 | 6.4201 | 1.1225 | 298.15 | 0.92567 | 0.94187 | 3.2449 | 3.9977 | 27.8007 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.10472 | 0.10472 | 12.8018 | 435 | 440.26 | 1.0629 | 1.0646 | 298.15 | 0.32963 | 0.35298 | 1.1153 | 453 | 2816.5993 | 6.5855 | 0.95671 | 1.0583 | 21.47 | 124.0139 | 0.4195 | 0.077088 | 0.077088 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 107.3542 | 49.2893 | 0.17052 | 0.3326 | 0.5173 | 107.3542 | 66.1261 | 0.22662 | 0.34451 | 0.53583 | 5.7504 | 4.949 | 0.66417 | 0.57153 | 0.96425 | 1.0725 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 50.3414 | 0.18123 | 40.6865 | 0.14647 | 9.3417 | 0.03363 | 0.11825 | 9.7797 | 0.035207 | 0.12379 | 0.082845 | 0.0713 | 298.2436 | 256.6817 | 0.0063727 | 0.0054839 | 22.9419 | 19.7419 | 0.016464 | 0.016458 | 59.2719 | 59.2481 | 8.9953 | 8.9467 | 3.2449 | 4.0853 | 1.4928 | 1.5251 | 0.85199 | 0.95359 | 0.95671 | 1.0583 | 0.3326 | 0.5173 | 19.2219 | 3244.8894 | 3997.7177 | 1.1153 | 1.2338 | 107.3542 | 166.9708 | 0.29231 | 0.36013 | 0.26988 | 0.29854 | 0.77517 | 1.1465 | 0.27577 | 0.33975 | 0.56194 | 0.62526 | 0.4888 | 0.34765 | 0.14647 | 0.12379 | 380.4574 | 335.6717
2013-04-05 | 66 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 27122.0119 | 19 | 78489.67 | 17 | 2 | 5 | 403.4563 | 101.3726 | 180 | 3.9791 | 17 | 1250 | 94565.0496 | 11662.1393 | 337.461 | 11.8822 | 15.5459 | 37 | 29.7383 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 7.2617 | 180 | 3.6638 | 12.6874 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0737 | 478.0258 | 1149.9681 |  | 671.9423 | 10889.903 | 3270.4029 | 1130.0838 | 0.22328 | 19.8506 | 28.1591 | 0.02 | 0.05 | 30 | 165 | 453 | 676.4563 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 655.4724 | 32.4432 | 1.1252 | 1.0216 | 198.9423 | 473 | 438 | 440.5568 | 235.8995 | 0.2189 | 0.027 | 1.06 | 11.8378 | 11.8378 | 676.4563 | 671.9423 | 1.1252 | 1.124 | 2.8993 | 2.8417 | 676.4563 | 671.9423 | 12.8027 | 1.1252 | 1.124 | 298.15 | 1.9309 | 1.8926 | 676.4563 | 6.4206 | 1.1252 | 298.15 | 0.96836 | 0.94914 | 3.2704 | 4.0261 | 28.1591 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.10607 | 0.10607 | 12.8027 | 435 | 440.5568 | 1.0629 | 1.0646 | 298.15 | 0.32965 | 0.35433 | 1.1053 | 453 | 2816.5993 | 6.5855 | 0.9481 | 1.0701 | 21.47 | 124.5424 | 0.42126 | 0.077163 | 0.077163 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 94.4891 | 49.8126 | 0.17227 | 0.29307 | 0.57878 | 94.4891 | 65.1459 | 0.22336 | 0.30261 | 0.59763 | 5.6682 | 4.97 | 0.75923 | 0.57425 | 0.95335 | 1.0846 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 49.699 | 0.17892 | 40.5769 | 0.14608 | 9.2354 | 0.033248 | 0.1169 | 9.9105 | 0.035678 | 0.12545 | 0.081661 | 0.071603 | 293.9806 | 257.7724 | 0.0072849 | 0.00551 | 26.2257 | 19.8359 | 0.017395 | 0.016607 | 62.6236 | 59.7839 | 8.9386 | 8.9961 | 3.2704 | 3.9232 | 1.5766 | 1.5383 | 0.84203 | 0.96402 | 0.9481 | 1.0701 | 0.29307 | 0.57878 | 19.2233 | 3270.4029 | 4026.0501 | 1.1053 | 1.2475 | 94.4891 | 186.6048 | 0.29284 | 0.36051 | 0.26585 | 0.30005 | 0.64265 | 0.97721 | 0.27627 | 0.3401 | 0.52585 | 0.62669 | 0.54087 | 0.30911 | 0.14608 | 0.12545 | 382.8299 | 337.3922
2013-04-09 | 67 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 27312.9471 | 19 | 79064.2386 | 17 | 2 | 5 | 394.5443 | 106.0074 | 180 | 4.3228 | 17 | 1250 | 20791.2725 | 2895.4471 | 89.9725 | 24.2676 | 24.7534 | 37 | 30.3006 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 6.6994 | 180 | 0.48576 | 12.6884 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.074 | 479.4436 | 1153.3789 |  | 673.9353 | 10923.0949 | 3294.3433 | 1138.0395 | 0.22486 | 5.2925 | 29.4465 | 0.02 | 0.05 | 30 | 165 | 453 | 667.5443 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 712.0852 | 35.2424 | 1.1228 | 1.0205 | 200.9353 | 473 | 438 | 437.7576 | 229.7868 | 0.2189 | 0.027 | 1.06 | 11.9212 | 11.9212 | 667.5443 | 673.9353 | 1.1228 | 1.1245 | 2.7863 | 2.8673 | 667.5443 | 673.9353 | 12.8038 | 1.1228 | 1.1245 | 298.15 | 1.8557 | 1.9096 | 667.5443 | 6.4211 | 1.1228 | 298.15 | 0.93063 | 0.95769 | 3.2943 | 4.0592 | 29.4465 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.11092 | 0.11092 | 12.8038 | 435 | 437.7576 | 1.0631 | 1.064 | 298.15 | 0.32973 | 0.3419 | 1.2008 | 453 | 2816.5993 | 6.5855 | 1.03 | 1.0786 | 21.47 | 126.8959 | 0.4291 | 0.077496 | 0.077496 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 25.1923 | 101.6471 | 0.34498 | 0.086741 | 4.9789 | 25.1923 | 103.68 | 0.35175 | 0.087078 | 4.9982 | 5.8405 | 4.9946 | 0.60688 | 0.60007 | 1.0264 | 1.094 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 50.1962 | 0.18071 | 40.45 | 0.14562 | 5.9444 | 0.0214 | 0.075246 | 10.5882 | 0.038117 | 0.13403 | 0.084144 | 0.071957 | 302.9195 | 259.0464 | 0.0058231 | 0.0057577 | 20.9631 | 20.7277 | 0.016351 | 0.017006 | 58.8631 | 61.2227 | 9.1349 | 9.0539 | 3.2943 | 4.2048 | 1.5138 | 1.5677 | 0.91907 | 0.96767 | 1.03 | 1.0786 | 0.086741 | 4.9789 | 19.2249 | 3294.3433 | 4059.242 | 1.2008 | 1.2574 | 25.1923 | 1446.0276 | 0.29292 | 0.36094 | 0.28679 | 0.30033 | 0.7257 | 0.075267 | 0.27634 | 0.34051 | 0.60229 | 0.61724 | 4.6161 | 0.084215 | 0.14562 | 0.13403 | 382.7457 | 340.9967
2013-04-10 | 68 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 26430.476 | 19 | 75458.5253 | 17 | 2 | 5 | 396.5415 | 96.8407 | 180 | 3.898 | 17 | 1250 | 56380.4355 | 7613.485 | 323.5924 | 12.1469 | 14.9668 | 37 | 27.4375 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 9.5625 | 180 | 2.8199 | 12.6836 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0724 | 472.8888 | 1137.6103 |  | 664.7215 | 10769.6873 | 3144.1052 | 1101.2698 | 0.21759 | 19.0348 | 26.9002 | 0.02 | 0.05 | 30 | 165 | 453 | 669.5415 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 642.1177 | 31.7916 | 1.1233 | 1.0203 | 191.7215 | 473 | 438 | 441.2084 | 228.3331 | 0.2189 | 0.027 | 1.06 | 11.536 | 11.536 | 669.5415 | 664.7215 | 1.1233 | 1.122 | 2.8105 | 2.7498 | 669.5415 | 664.7215 | 12.7989 | 1.1233 | 1.122 | 298.15 | 1.8718 | 1.8313 | 669.5415 | 6.4187 | 1.1233 | 298.15 | 0.9387 | 0.91842 | 3.1441 | 3.9058 | 26.9002 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.10133 | 0.10133 | 12.7989 | 435 | 441.2084 | 1.0629 | 1.0648 | 298.15 | 0.32953 | 0.35715 | 1.0828 | 453 | 2816.5993 | 6.5855 | 0.92879 | 1.0292 | 21.47 | 114.9133 | 0.38918 | 0.075801 | 0.075801 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 90.6059 | 50.9205 | 0.17596 | 0.28169 | 0.66395 | 90.6059 | 62.7221 | 0.21528 | 0.28873 | 0.68056 | 5.5814 | 4.8804 | 0.71479 | 0.54628 | 0.93017 | 1.0402 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 50.7192 | 0.18259 | 41.0517 | 0.14779 | 8.9904 | 0.032365 | 0.1138 | 9.7951 | 0.035262 | 0.12399 | 0.080412 | 0.070312 | 289.4815 | 253.1236 | 0.0068584 | 0.0052415 | 24.6904 | 18.8696 | 0.016635 | 0.015856 | 59.8854 | 57.0831 | 8.7255 | 8.7862 | 3.1441 | 3.7961 | 1.5146 | 1.4742 | 0.82746 | 0.92791 | 0.92879 | 1.0292 | 0.28169 | 0.66395 | 19.2176 | 3144.1052 | 3905.8344 | 1.0828 | 1.1999 | 90.6059 | 213.5642 | 0.2889 | 0.35889 | 0.26723 | 0.29614 | 0.70369 | 0.396 | 0.27255 | 0.33858 | 0.53653 | 0.62944 | 0.64509 | 0.30328 | 0.14779 | 0.12399 | 374.0573 | 329.0762
2013-04-11 | 69 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 26641.9247 | 19 | 76125.7556 | 17 | 2 | 5 | 388.3418 | 72.5101 | 180 | 2.8994 | 17 | 1250 | 62917.5643 | 9325.1515 | 331.1019 | 11.2368 | 14.0497 | 37 | 27.7658 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 9.2342 | 180 | 2.8128 | 12.6848 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0728 | 474.4599 | 1141.3897 |  | 666.9298 | 10806.4452 | 3171.9065 | 1110.0802 | 0.21933 | 19.4766 | 20.1417 | 0.02 | 0.05 | 30 | 165 | 453 | 661.3418 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 477.616 | 23.6449 | 1.1211 | 1.0175 | 193.9298 | 473 | 438 | 449.3551 | 211.9867 | 0.2189 | 0.027 | 1.06 | 11.6283 | 11.6283 | 661.3418 | 666.9298 | 1.1211 | 1.1226 | 2.7077 | 2.7778 | 661.3418 | 666.9298 | 12.8001 | 1.1211 | 1.1226 | 298.15 | 1.8033 | 1.85 | 661.3418 | 6.4193 | 1.1211 | 298.15 | 0.90438 | 0.92778 | 3.1719 | 3.9426 | 20.1417 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.075871 | 0.075871 | 12.8001 | 435 | 449.3551 | 1.0623 | 1.0667 | 298.15 | 0.32938 | 0.39459 | 0.80539 | 453 | 2816.5993 | 6.5855 | 0.69084 | 1.0392 | 21.47 | 116.2873 | 0.39376 | 0.075995 | 0.075995 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 92.7085 | 47.1119 | 0.16327 | 0.2859 | 0.6765 | 92.7085 | 58.8839 | 0.20249 | 0.29309 | 0.69352 | 5.7487 | 4.9079 | 0.85898 | 0.49213 | 0.69257 | 1.0507 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 51.1606 | 0.18418 | 40.9039 | 0.14725 | 9.0529 | 0.03259 | 0.11459 | 9.869 | 0.035528 | 0.12492 | 0.082821 | 0.070709 | 298.1565 | 254.5509 | 0.008242 | 0.004722 | 29.6711 | 16.9991 | 0.015927 | 0.015232 | 57.3378 | 54.8353 | 8.9206 | 8.8505 | 3.1719 | 4.0699 | 1.4087 | 1.4554 | 0.61497 | 0.96328 | 0.69084 | 1.0392 | 0.2859 | 0.6765 | 19.2193 | 3171.9065 | 3942.5924 | 0.80539 | 1.2114 | 92.7085 | 219.3712 | 0.28914 | 0.35939 | 0.1972 | 0.29662 | 0.77234 | 0.41557 | 0.27277 | 0.33905 | 0.41723 | 0.66186 | 0.65101 | 0.41384 | 0.14725 | 0.12492 | 385.1654 | 326.3853
2013-04-12 | 70 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 26920.2144 | 19 | 77400.0306 | 17 | 2 | 5 | 382.3846 | 76.1006 | 180 | 3.0072 | 17 | 1250 | 66674.1653 | 9958.078 | 338.4775 | 11.589 | 14.7867 | 37 | 27.9676 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 9.0324 | 180 | 3.1977 | 12.6863 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0733 | 476.5271 | 1146.3628 |  | 669.8357 | 10854.8228 | 3225.0013 | 1121.6756 | 0.22162 | 19.9104 | 21.1391 | 0.02 | 0.05 | 30 | 165 | 453 | 655.3846 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 495.3765 | 24.5213 | 1.1195 | 1.0166 | 196.8357 | 473 | 438 | 448.4787 | 206.9059 | 0.2189 | 0.027 | 1.06 | 11.7498 | 11.7498 | 655.3846 | 669.8357 | 1.1195 | 1.1234 | 2.634 | 2.8148 | 655.3846 | 669.8357 | 12.8016 | 1.1195 | 1.1234 | 298.15 | 1.7543 | 1.8747 | 655.3846 | 6.42 | 1.1195 | 298.15 | 0.87977 | 0.94014 | 3.225 | 3.991 | 21.1391 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.079628 | 0.079628 | 12.8016 | 435 | 448.4787 | 1.0623 | 1.0665 | 298.15 | 0.32944 | 0.39054 | 0.83534 | 453 | 2816.5993 | 6.5855 | 0.71653 | 1.0533 | 21.47 | 117.1319 | 0.39657 | 0.076115 | 0.076115 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 94.7737 | 48.5857 | 0.16818 | 0.29318 | 0.61191 | 94.7737 | 61.9685 | 0.21277 | 0.30154 | 0.62935 | 5.8907 | 4.944 | 0.78792 | 0.51039 | 0.71954 | 1.0654 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 51.19 | 0.18428 | 40.7129 | 0.14657 | 9.1512 | 0.032944 | 0.11584 | 9.8888 | 0.0356 | 0.12517 | 0.084868 | 0.071228 | 305.5234 | 256.4215 | 0.0075602 | 0.0048972 | 27.2167 | 17.6301 | 0.015445 | 0.015582 | 55.6026 | 56.0934 | 9.1157 | 8.935 | 3.225 | 4.3201 | 1.3637 | 1.4841 | 0.63691 | 0.97372 | 0.71653 | 1.0533 | 0.29318 | 0.61191 | 19.2216 | 3225.0013 | 3990.9699 | 0.83534 | 1.228 | 94.7737 | 197.8041 | 0.29094 | 0.36004 | 0.20242 | 0.29757 | 0.77829 | 0.52055 | 0.27447 | 0.33966 | 0.447 | 0.6561 | 0.58092 | 0.40917 | 0.14657 | 0.12517 | 388.3427 | 330.145
2013-04-13 | 71 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 26176.0603 | 19 | 74459.8908 | 17 | 2 | 5 | 381.3229 | 76.1206 | 180 | 3.1399 | 17 | 1250 | 72135.2771 | 10137.5235 | 346.6841 | 11.2278 | 14.6144 | 37 | 28.9914 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 8.0086 | 180 | 3.3866 | 12.6822 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.072 | 470.9982 | 1133.0621 |  | 662.0639 | 10725.4599 | 3102.4955 | 1090.6692 | 0.2155 | 20.3932 | 21.1446 | 0.02 | 0.05 | 30 | 165 | 453 | 654.3229 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 517.2292 | 25.6111 | 1.1192 | 1.0166 | 189.0639 | 473 | 438 | 447.3889 | 206.934 | 0.2189 | 0.027 | 1.06 | 11.425 | 11.425 | 654.3229 | 662.0639 | 1.1192 | 1.1213 | 2.6201 | 2.7162 | 654.3229 | 662.0639 | 12.7975 | 1.1192 | 1.1213 | 298.15 | 1.745 | 1.809 | 654.3229 | 6.418 | 1.1192 | 298.15 | 0.87511 | 0.90721 | 3.1025 | 3.8616 | 21.1446 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.079649 | 0.079649 | 12.7975 | 435 | 447.3889 | 1.0624 | 1.0663 | 298.15 | 0.32936 | 0.38535 | 0.87219 | 453 | 2816.5993 | 6.5855 | 0.74814 | 1.0112 | 21.47 | 121.4165 | 0.41085 | 0.076721 | 0.076721 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 97.0716 | 47.074 | 0.16314 | 0.29933 | 0.56581 | 97.0716 | 61.2473 | 0.21037 | 0.30839 | 0.58295 | 5.7024 | 4.8472 | 0.74713 | 0.4921 | 0.75247 | 1.0236 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 51.7678 | 0.18636 | 41.2329 | 0.14844 | 8.984 | 0.032342 | 0.11372 | 9.6165 | 0.034619 | 0.12173 | 0.082154 | 0.069833 | 295.7548 | 251.3994 | 0.0071687 | 0.0047218 | 25.8075 | 16.9984 | 0.015289 | 0.01501 | 55.0412 | 54.0343 | 8.8049 | 8.7088 | 3.1025 | 4.0379 | 1.3596 | 1.4236 | 0.66849 | 0.93153 | 0.74814 | 1.0112 | 0.29933 | 0.56581 | 19.2155 | 3102.4955 | 3861.6071 | 0.87219 | 1.1788 | 97.0716 | 183.4925 | 0.28785 | 0.35828 | 0.21735 | 0.29376 | 0.73233 | 0.70011 | 0.27155 | 0.338 | 0.47223 | 0.65433 | 0.55956 | 0.40009 | 0.14844 | 0.12173 | 376.6035 | 322.4321
2013-04-14 | 72 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 25633.7463 | 19 | 71496.7189 | 17 | 2 | 5 | 394.1721 | 82.7115 | 180 | 3.2946 | 17 | 1250 | 76708.8331 | 10976.1784 | 359.2577 | 9.6731 | 12.7138 | 37 | 28.613 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 8.387 | 180 | 3.0406 | 12.6793 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.071 | 466.9667 | 1123.3636 |  | 656.3969 | 10631.1848 | 2979.03 | 1068.0728 | 0.21103 | 21.1328 | 22.9754 | 0.02 | 0.05 | 30 | 165 | 453 | 667.1721 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 542.7204 | 26.8796 | 1.1227 | 1.019 | 183.3969 | 473 | 438 | 446.1204 | 221.0517 | 0.2189 | 0.027 | 1.06 | 11.1883 | 11.1883 | 667.1721 | 656.3969 | 1.1227 | 1.1198 | 2.7796 | 2.6451 | 667.1721 | 656.3969 | 12.7945 | 1.1227 | 1.1198 | 298.15 | 1.8512 | 1.7616 | 667.1721 | 6.4165 | 1.1227 | 298.15 | 0.92839 | 0.88346 | 2.979 | 3.7673 | 22.9754 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.086546 | 0.086546 | 12.7945 | 435 | 446.1204 | 1.0625 | 1.066 | 298.15 | 0.32931 | 0.3794 | 0.91518 | 453 | 2816.5993 | 6.5855 | 0.78501 | 0.98366 | 21.47 | 119.833 | 0.40557 | 0.076497 | 0.076497 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 100.5921 | 40.5676 | 0.14146 | 0.30587 | 0.59172 | 100.5921 | 53.293 | 0.18386 | 0.3143 | 0.60803 | 5.4296 | 4.7758 | 0.82345 | 0.48513 | 0.78848 | 0.99501 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 51.9971 | 0.18719 | 41.6313 | 0.14987 | 8.8889 | 0.032 | 0.11252 | 9.4872 | 0.034154 | 0.12009 | 0.078224 | 0.068805 | 281.6077 | 247.6992 | 0.007901 | 0.0046549 | 28.4438 | 16.7575 | 0.016485 | 0.01471 | 59.3454 | 52.9559 | 8.4086 | 8.5432 | 2.979 | 3.522 | 1.4718 | 1.3822 | 0.69847 | 0.89711 | 0.78501 | 0.98366 | 0.30587 | 0.59172 | 19.211 | 2979.03 | 3767.3319 | 0.91518 | 1.1468 | 100.5921 | 194.5997 | 0.28224 | 0.35693 | 0.23288 | 0.2918 | 0.74564 | 0.54222 | 0.26626 | 0.33672 | 0.45894 | 0.64903 | 0.60155 | 0.38964 | 0.14987 | 0.12009 | 369.3968 | 317.4126
2013-04-15 | 73 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 27518.5751 | 19 | 79887.3033 | 17 | 2 | 5 | 387.4753 | 88.4574 | 180 | 3.4679 | 17 | 1250 | 76495.6865 | 10501.7531 | 338.4116 | 9.5656 | 13.021 | 37 | 28.9618 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 8.0382 | 180 | 3.4554 | 12.6895 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0744 | 480.9702 | 1157.0515 |  | 676.0812 | 10958.841 | 3328.6376 | 1146.6073 | 0.22655 | 19.9066 | 24.5715 | 0.02 | 0.05 | 30 | 165 | 453 | 660.4753 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 571.2639 | 28.2704 | 1.1209 | 1.0181 | 203.0812 | 473 | 438 | 444.7296 | 215.7458 | 0.2189 | 0.027 | 1.06 | 12.0109 | 12.0109 | 660.4753 | 676.0812 | 1.1209 | 1.1251 | 2.6979 | 2.895 | 660.4753 | 676.0812 | 12.8049 | 1.1209 | 1.1251 | 298.15 | 1.7968 | 1.928 | 660.4753 | 6.4217 | 1.1209 | 298.15 | 0.9011 | 0.96692 | 3.3286 | 4.095 | 24.5715 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.092558 | 0.092558 | 12.8049 | 435 | 444.7296 | 1.0626 | 1.0656 | 298.15 | 0.32961 | 0.37331 | 0.96331 | 453 | 2816.5993 | 6.5855 | 0.8263 | 1.0884 | 21.47 | 121.2927 | 0.41043 | 0.076703 | 0.076703 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 94.7552 | 40.1177 | 0.13997 | 0.28784 | 0.59899 | 94.7552 | 54.579 | 0.18815 | 0.29687 | 0.61778 | 5.9844 | 5.021 | 0.73346 | 0.55892 | 0.83057 | 1.1024 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 50.4501 | 0.18162 | 40.3155 | 0.14514 | 9.2882 | 0.033437 | 0.11757 | 10.0511 | 0.036184 | 0.12723 | 0.086217 | 0.072337 | 310.3806 | 260.4137 | 0.0070376 | 0.0053629 | 25.3353 | 19.3065 | 0.015936 | 0.016515 | 57.3684 | 59.4523 | 9.313 | 9.116 | 3.3286 | 4.4506 | 1.4235 | 1.5547 | 0.73374 | 0.99581 | 0.8263 | 1.0884 | 0.28784 | 0.59899 | 19.2265 | 3328.6376 | 4094.9882 | 0.96331 | 1.2688 | 94.7552 | 197.1831 | 0.29376 | 0.36139 | 0.22836 | 0.30079 | 0.7154 | 0.72032 | 0.27713 | 0.34094 | 0.5001 | 0.6405 | 0.55035 | 0.34835 | 0.14514 | 0.12723 | 393.0844 | 339.1725
2013-04-16 | 74 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 27672.0732 | 19 | 80763.1542 | 17 | 2 | 5 | 389.5191 | 96.2581 | 180 | 3.9751 | 17 | 1250 | 78599.9654 | 11208.4396 | 331.0648 | 11.6709 | 15.1096 | 37 | 29.1142 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 7.8858 | 180 | 3.4387 | 12.6904 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0747 | 482.1097 | 1159.7926 |  | 677.6829 | 10985.5249 | 3365.1314 | 1153.0031 | 0.22781 | 19.4744 | 26.7384 | 0.02 | 0.05 | 30 | 165 | 453 | 662.5191 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 654.8055 | 32.4026 | 1.1214 | 1.0192 | 204.6829 | 473 | 438 | 440.5974 | 221.9217 | 0.2189 | 0.027 | 1.06 | 12.0779 | 12.0779 | 662.5191 | 677.6829 | 1.1214 | 1.1255 | 2.7236 | 2.9157 | 662.5191 | 677.6829 | 12.8057 | 1.1214 | 1.1255 | 298.15 | 1.8139 | 1.9418 | 662.5191 | 6.4221 | 1.1214 | 298.15 | 0.90969 | 0.97383 | 3.3651 | 4.1217 | 26.7384 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.10072 | 0.10072 | 12.8057 | 435 | 440.5974 | 1.0629 | 1.0646 | 298.15 | 0.32972 | 0.3546 | 1.1042 | 453 | 2816.5993 | 6.5855 | 0.94714 | 1.0976 | 21.47 | 121.9307 | 0.41256 | 0.076794 | 0.076794 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 92.6981 | 48.9284 | 0.16932 | 0.28697 | 0.62284 | 92.6981 | 63.3199 | 0.21727 | 0.29576 | 0.64191 | 5.9892 | 5.0406 | 0.63779 | 0.59039 | 0.95126 | 1.112 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 50.0798 | 0.18029 | 40.2163 | 0.14478 | 9.3267 | 0.033576 | 0.11806 | 10.1227 | 0.036442 | 0.12814 | 0.086286 | 0.07262 | 310.6295 | 261.4313 | 0.0061196 | 0.0056648 | 22.0307 | 20.3933 | 0.016005 | 0.016988 | 57.6181 | 61.1585 | 9.3543 | 9.1623 | 3.3651 | 4.4672 | 1.4593 | 1.5872 | 0.84642 | 0.99684 | 0.94714 | 1.0976 | 0.28697 | 0.62284 | 19.2278 | 3365.1314 | 4121.6721 | 1.1042 | 1.2795 | 92.6981 | 201.1887 | 0.29534 | 0.36173 | 0.26031 | 0.30165 | 0.7431 | 0.73938 | 0.27862 | 0.34126 | 0.57028 | 0.62804 | 0.56747 | 0.30299 | 0.14478 | 0.12814 | 390.2783 | 342.9832
2013-04-17 | 75 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 26585.754 | 19 | 75907.5981 | 17 | 2 | 5 | 398.09 | 90.3716 | 180 | 3.6458 | 17 | 1250 | 84003.0969 | 12641.1235 | 359.4279 | 10.9974 | 15.0943 | 37 | 28.8001 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 8.1999 | 180 | 4.0968 | 12.6845 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0727 | 474.0426 | 1140.3858 |  | 666.3432 | 10796.6806 | 3162.8166 | 1107.7398 | 0.21887 | 21.1428 | 25.1032 | 0.02 | 0.05 | 30 | 165 | 453 | 671.09 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 600.5724 | 29.7327 | 1.1237 | 1.0202 | 193.3432 | 473 | 438 | 443.2673 | 227.8228 | 0.2189 | 0.027 | 1.06 | 11.6038 | 11.6038 | 671.09 | 666.3432 | 1.1237 | 1.1225 | 2.8303 | 2.7703 | 671.09 | 666.3432 | 12.7998 | 1.1237 | 1.1225 | 298.15 | 1.885 | 1.845 | 671.09 | 6.4191 | 1.1237 | 298.15 | 0.94531 | 0.92529 | 3.1628 | 3.9328 | 25.1032 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.094561 | 0.094561 | 12.7998 | 435 | 443.2673 | 1.0627 | 1.0653 | 298.15 | 0.32951 | 0.36649 | 1.0127 | 453 | 2816.5993 | 6.5855 | 0.86869 | 1.0384 | 21.47 | 120.6161 | 0.40818 | 0.076608 | 0.076608 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 100.6398 | 46.11 | 0.15993 | 0.30969 | 0.47972 | 100.6398 | 63.2557 | 0.21706 | 0.32106 | 0.49733 | 5.6107 | 4.9006 | 0.78132 | 0.53471 | 0.87521 | 1.0512 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 50.6376 | 0.1823 | 40.9429 | 0.14739 | 9.1604 | 0.032977 | 0.11595 | 9.6103 | 0.034597 | 0.12165 | 0.080833 | 0.070603 | 290.9994 | 254.1722 | 0.0074968 | 0.0051305 | 26.9886 | 18.4699 | 0.016873 | 0.0158 | 60.744 | 56.8793 | 8.7735 | 8.8335 | 3.1628 | 3.8247 | 1.5185 | 1.4785 | 0.77413 | 0.94384 | 0.86869 | 1.0384 | 0.30969 | 0.47972 | 19.2189 | 3162.8166 | 3932.8277 | 1.0127 | 1.2106 | 100.6398 | 155.8937 | 0.28892 | 0.35926 | 0.24849 | 0.29703 | 0.78418 | 0.953 | 0.27257 | 0.33893 | 0.49769 | 0.63836 | 0.46198 | 0.3565 | 0.14739 | 0.12165 | 378.732 | 329.5215
2013-04-18 | 76 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 26844.7698 | 19 | 76169.8622 | 17 | 2 | 5 | 303.8246 | 32.2999 | 180 | 1.4946 | 17 | 1250 | 79631.929 | 11787.7765 | 324.7389 | 10.8317 | 14.9028 | 37 | 28.5014 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 8.4986 | 180 | 4.0711 | 12.6859 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0732 | 475.9667 | 1145.0147 |  | 669.048 | 10841.7076 | 3173.7443 | 1118.5321 | 0.221 | 19.1023 | 8.9722 | 0.02 | 0.05 | 30 | 165 | 453 | 576.8246 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 246.1983 | 12.1873 | 1.0987 | 1.0032 | 196.048 | 473 | 438 | 460.8127 | 116.0119 | 0.2189 | 0.027 | 1.06 | 11.7168 | 11.7168 | 576.8246 | 669.048 | 1.0987 | 1.1232 | 1.7299 | 2.8047 | 576.8246 | 669.048 | 12.8012 | 1.0987 | 1.1232 | 298.15 | 1.1521 | 1.868 | 576.8246 | 6.4198 | 1.0987 | 298.15 | 0.57779 | 0.93678 | 3.1737 | 3.9779 | 8.9722 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.033797 | 0.033797 | 12.8012 | 435 | 460.8127 | 1.0614 | 1.0695 | 298.15 | 0.32914 | 0.44973 | 0.41516 | 453 | 2816.5993 | 6.5855 | 0.35611 | 1.0296 | 21.47 | 119.3659 | 0.40401 | 0.076431 | 0.076431 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 90.9269 | 45.4163 | 0.15762 | 0.27939 | 0.47199 | 90.9269 | 62.4544 | 0.21439 | 0.28959 | 0.48923 | 6.8132 | 4.9342 | 0.50067 | 0.42241 | 0.36129 | 1.0418 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 55.9715 | 0.2015 | 40.7642 | 0.14675 | 8.9473 | 0.03221 | 0.11326 | 9.6718 | 0.034818 | 0.12243 | 0.098157 | 0.071088 | 353.3666 | 255.9152 | 0.004804 | 0.004053 | 17.2943 | 14.5908 | 0.0088514 | 0.014237 | 31.8651 | 51.252 | 9.9869 | 8.9121 | 3.1737 | 6.0785 | 0.70239 | 1.4182 | 0.32231 | 0.99582 | 0.35611 | 1.0296 | 0.27939 | 0.47199 | 19.221 | 3173.7443 | 3977.8547 | 0.41516 | 1.2003 | 90.9269 | 153.6095 | 0.28712 | 0.35987 | 0.10089 | 0.29169 | 0.77138 | 0.87609 | 0.27087 | 0.3395 | 0.39164 | 0.70216 | 0.45841 | 0.78455 | 0.14675 | 0.12243 | 402.526 | 321.758
2013-04-19 | 77 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 24082.3434 | 19 | 64358.095 | 17 | 2 | 5 | 365.8747 | 72.65 | 180 | 2.9728 | 17 | 1250 | 76542.4682 | 9924.3374 | 279.2432 | 9.5786 | 13.7003 | 37 | 28.9329 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 8.0671 | 180 | 4.1217 | 12.6709 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0682 | 455.4234 | 1095.5943 |  | 640.1709 | 10361.4909 | 2681.5873 | 1003.431 | 0.19826 | 16.4261 | 20.1806 | 0.02 | 0.05 | 30 | 165 | 453 | 638.8747 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 489.7029 | 24.2699 | 1.1151 | 1.0139 | 167.1709 | 473 | 438 | 448.7301 | 190.1446 | 0.2189 | 0.027 | 1.06 | 10.5111 | 10.5111 | 638.8747 | 640.1709 | 1.1151 | 1.1155 | 2.4299 | 2.4454 | 638.8747 | 640.1709 | 12.786 | 1.1151 | 1.1155 | 298.15 | 1.6183 | 1.6287 | 638.8747 | 6.4122 | 1.1151 | 298.15 | 0.81158 | 0.81678 | 2.6816 | 3.4976 | 20.1806 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.076018 | 0.076018 | 12.786 | 435 | 448.7301 | 1.0623 | 1.0666 | 298.15 | 0.32903 | 0.39124 | 0.82577 | 453 | 2816.5993 | 6.5855 | 0.70833 | 0.88999 | 21.47 | 121.1719 | 0.41003 | 0.076686 | 0.076686 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 78.1881 | 40.1718 | 0.14015 | 0.23754 | 0.38703 | 78.1881 | 57.4216 | 0.19762 | 0.24643 | 0.40151 | 5.3997 | 4.568 | 0.65695 | 0.42345 | 0.71244 | 0.89969 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 56.0058 | 0.20162 | 42.8747 | 0.15435 | 8.0914 | 0.029129 | 0.10242 | 8.6981 | 0.031313 | 0.1101 | 0.077793 | 0.065812 | 280.0549 | 236.9226 | 0.0063035 | 0.0040631 | 22.6925 | 14.627 | 0.013938 | 0.013124 | 50.1774 | 47.2448 | 8.0813 | 8.0657 | 2.6816 | 3.5271 | 1.2271 | 1.2374 | 0.63231 | 0.81397 | 0.70833 | 0.88999 | 0.23754 | 0.38703 | 19.1983 | 2681.5873 | 3497.638 | 0.82577 | 1.0376 | 78.1881 | 127.3939 | 0.27043 | 0.35272 | 0.22364 | 0.28099 | 0.67565 | 0.99786 | 0.25512 | 0.33276 | 0.49044 | 0.65779 | 0.43488 | 0.33536 | 0.15435 | 0.1101 | 352.9248 | 298.7945
2013-04-22 | 79 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 27350.9536 | 19 | 78743.3208 | 17 | 2 | 5 | 383.7423 | 84.0262 | 180 | 3.2558 | 17 | 1250 | 80340.3728 | 11383.7282 | 359.7767 | 10.9857 | 14.4314 | 37 | 28.772 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 8.228 | 180 | 3.4457 | 12.6886 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0741 | 479.7258 | 1154.0577 |  | 674.3319 | 10929.7019 | 3280.9717 | 1139.6231 | 0.22517 | 21.1633 | 23.3406 | 0.02 | 0.05 | 30 | 165 | 453 | 656.7423 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 536.3264 | 26.5434 | 1.1199 | 1.0172 | 201.3319 | 473 | 438 | 446.4566 | 210.2857 | 0.2189 | 0.027 | 1.06 | 11.9378 | 11.9378 | 656.7423 | 674.3319 | 1.1199 | 1.1246 | 2.6513 | 2.8724 | 656.7423 | 674.3319 | 12.804 | 1.1199 | 1.1246 | 298.15 | 1.7658 | 1.913 | 656.7423 | 6.4212 | 1.1199 | 298.15 | 0.88554 | 0.95939 | 3.281 | 4.0658 | 23.3406 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.087921 | 0.087921 | 12.804 | 435 | 446.4566 | 1.0625 | 1.066 | 298.15 | 0.32955 | 0.38123 | 0.90439 | 453 | 2816.5993 | 6.5855 | 0.77577 | 1.078 | 21.47 | 120.4984 | 0.40779 | 0.076591 | 0.076591 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 100.7375 | 46.0607 | 0.15977 | 0.30996 | 0.59748 | 100.7375 | 60.4814 | 0.20782 | 0.31953 | 0.61593 | 6.0055 | 4.9995 | 0.74839 | 0.54178 | 0.78047 | 1.0915 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 51.0664 | 0.18384 | 40.425 | 0.14553 | 9.3419 | 0.033631 | 0.11825 | 9.9999 | 0.036 | 0.12658 | 0.086521 | 0.072028 | 311.4746 | 259.2995 | 0.0071809 | 0.0051984 | 25.8512 | 18.7141 | 0.015636 | 0.016205 | 56.2912 | 58.3367 | 9.2864 | 9.0653 | 3.281 | 4.4666 | 1.3846 | 1.5318 | 0.68784 | 0.99003 | 0.77577 | 1.078 | 0.30996 | 0.59748 | 19.2252 | 3280.9717 | 4065.849 | 0.90439 | 1.2567 | 100.7375 | 194.184 | 0.29133 | 0.36102 | 0.21571 | 0.29974 | 0.73837 | 0.68758 | 0.27484 | 0.34059 | 0.47892 | 0.64632 | 0.55427 | 0.39955 | 0.14553 | 0.12658 | 393.617 | 336.3503
2013-04-23 | 80 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 26529.6763 | 19 | 75903.9378 | 17 | 2 | 5 | 358.9944 | 63.8557 | 180 | 2.5594 | 17 | 1250 | 78383.9232 | 11057.2254 | 312.9785 | 9.8653 | 13.6203 | 37 | 28.3814 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 8.6186 | 180 | 3.7549 | 12.6841 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0726 | 473.6259 | 1139.3835 |  | 665.7576 | 10786.9321 | 3162.6641 | 1105.4032 | 0.21841 | 18.4105 | 17.7377 | 0.02 | 0.05 | 30 | 165 | 453 | 631.9944 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 421.6115 | 20.8734 | 1.1133 | 1.0123 | 192.7576 | 473 | 438 | 452.1266 | 179.8678 | 0.2189 | 0.027 | 1.06 | 11.5793 | 11.5793 | 631.9944 | 665.7576 | 1.1133 | 1.1223 | 2.3503 | 2.7629 | 631.9944 | 665.7576 | 12.7995 | 1.1133 | 1.1223 | 298.15 | 1.5653 | 1.8401 | 631.9944 | 6.4189 | 1.1133 | 298.15 | 0.785 | 0.9228 | 3.1627 | 3.9231 | 17.7377 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.066816 | 0.066816 | 12.7995 | 435 | 452.1266 | 1.0621 | 1.0674 | 298.15 | 0.3293 | 0.40764 | 0.71095 | 453 | 2816.5993 | 6.5855 | 0.60984 | 1.0256 | 21.47 | 118.8638 | 0.40234 | 0.07636 | 0.07636 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 87.634 | 41.372 | 0.14414 | 0.26693 | 0.50265 | 87.634 | 57.0869 | 0.19651 | 0.27601 | 0.51973 | 6.0664 | 4.8933 | 0.69297 | 0.47367 | 0.61381 | 1.0376 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 52.7151 | 0.18977 | 40.982 | 0.14754 | 8.8765 | 0.031956 | 0.11236 | 9.6319 | 0.034675 | 0.12192 | 0.087398 | 0.070498 | 314.6326 | 253.7938 | 0.0066491 | 0.0045449 | 23.9367 | 16.3615 | 0.013405 | 0.014874 | 48.2593 | 53.5465 | 9.229 | 8.8164 | 3.1627 | 4.692 | 1.1577 | 1.4324 | 0.54302 | 0.95878 | 0.60984 | 1.0256 | 0.26693 | 0.50265 | 19.2184 | 3162.6641 | 3923.0793 | 0.71095 | 1.1956 | 87.634 | 165.0186 | 0.28952 | 0.35913 | 0.17481 | 0.29399 | 0.7351 | 0.73507 | 0.27313 | 0.3388 | 0.43934 | 0.66933 | 0.4901 | 0.43771 | 0.14754 | 0.12192 | 386.8287 | 323.7019
2013-04-24 | 81 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 20081.1952 | 19 | 56428.6169 | 17 | 2 | 5 | 359.6084 | 82.1944 | 180 | 3.2351 | 17 | 1250 | 81053.0975 | 11353.0023 | 327.547 | 10.302 | 13.6578 | 37 | 28.6165 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 8.3835 | 180 | 3.3559 | 12.6491 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0611 | 425.5815 | 1023.805 |  | 598.2234 | 9665.9364 | 2351.1924 | 836.7165 | 0.16532 | 19.2675 | 22.8318 | 0.02 | 0.05 | 30 | 165 | 453 | 632.6084 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 532.9192 | 26.4571 | 1.1134 | 1.0132 | 125.2234 | 473 | 438 | 446.5429 | 186.0655 | 0.2189 | 0.027 | 1.06 | 8.7648 | 8.7648 | 632.6084 | 598.2234 | 1.1134 | 1.1043 | 2.3511 | 1.9567 | 632.6084 | 598.2234 | 12.7641 | 1.1134 | 1.1043 | 298.15 | 1.5658 | 1.3032 | 632.6084 | 6.4012 | 1.1134 | 298.15 | 0.78525 | 0.65355 | 2.3512 | 2.8021 | 22.8318 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.086004 | 0.086004 | 12.7641 | 435 | 446.5429 | 1.0625 | 1.0661 | 298.15 | 0.32852 | 0.38044 | 0.89865 | 453 | 2816.5993 | 6.5855 | 0.77084 | 0.66453 | 21.47 | 119.8477 | 0.40562 | 0.076499 | 0.076499 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 91.7132 | 43.1993 | 0.15023 | 0.28046 | 0.31109 | 91.7132 | 57.244 | 0.19703 | 0.28895 | 0.32051 | 4.0625 | 4.0059 | 0.55246 | 0.34423 | 0.77436 | 0.66898 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 53.6578 | 0.19317 | 47.051 | 0.16938 | 7.2909 | 0.026247 | 0.09229 | 7.3554 | 0.026479 | 0.093106 | 0.058529 | 0.057713 | 210.7027 | 207.7683 | 0.0053009 | 0.003303 | 19.0831 | 11.8906 | 0.013424 | 0.010238 | 48.3259 | 36.8578 | 6.4137 | 6.808 | 2.3512 | 2.0211 | 1.1854 | 0.92276 | 0.68483 | 0.57852 | 0.77084 | 0.66453 | 0.28046 | 0.31109 | 19.1653 | 2351.1924 | 2802.0836 | 0.89865 | 0.77471 | 91.7132 | 101.7297 | 0.28435 | 0.33888 | 0.29175 | 0.25152 | 0.7299 | 0.6364 | 0.26826 | 0.3197 | 0.55349 | 0.62695 | 0.46814 | 0.36384 | 0.16938 | 0.093106 | 278.1117 | 256.5166
2013-04-25 | 82 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 20934.8121 | 19 | 58712.5603 | 17 | 2 | 5 | 356.7415 | 72.5196 | 180 | 2.9049 | 17 | 1250 | 80081.6801 | 11397.2539 | 363.8258 | 10.5939 | 14.2327 | 37 | 28.7528 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 8.2472 | 180 | 3.6387 | 12.6537 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0626 | 431.9567 | 1039.1414 |  | 607.1847 | 9814.3281 | 2446.3567 | 872.2838 | 0.17235 | 21.4015 | 20.1443 | 0.02 | 0.05 | 30 | 165 | 453 | 629.7415 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 478.5261 | 23.748 | 1.1127 | 1.0124 | 134.1847 | 473 | 438 | 449.252 | 180.4896 | 0.2189 | 0.027 | 1.06 | 9.1373 | 9.1373 | 629.7415 | 607.1847 | 1.1127 | 1.1067 | 2.318 | 2.0577 | 629.7415 | 607.1847 | 12.7688 | 1.1127 | 1.1067 | 298.15 | 1.5438 | 1.3704 | 629.7415 | 6.4036 | 1.1127 | 298.15 | 0.77423 | 0.68728 | 2.4464 | 2.9505 | 20.1443 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.075881 | 0.075881 | 12.7688 | 435 | 449.252 | 1.0623 | 1.0667 | 298.15 | 0.32858 | 0.39315 | 0.80693 | 453 | 2816.5993 | 6.5855 | 0.69216 | 0.71186 | 21.47 | 120.4179 | 0.40752 | 0.07658 | 0.07658 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 101.8712 | 44.4213 | 0.1543 | 0.31235 | 0.32142 | 101.8712 | 59.6498 | 0.20504 | 0.32257 | 0.33194 | 4.3729 | 4.1291 | 0.59896 | 0.34133 | 0.6975 | 0.71749 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 53.9591 | 0.19425 | 46.0107 | 0.16564 | 7.6256 | 0.027452 | 0.096526 | 7.6262 | 0.027454 | 0.096534 | 0.063001 | 0.059488 | 226.8031 | 214.158 | 0.0057471 | 0.0032751 | 20.6894 | 11.7903 | 0.013197 | 0.010579 | 47.5093 | 38.0853 | 6.8193 | 7.0796 | 2.4464 | 2.438 | 1.1507 | 0.9773 | 0.61628 | 0.63597 | 0.69216 | 0.71186 | 0.31235 | 0.32142 | 19.1723 | 2446.3567 | 2950.4752 | 0.80693 | 0.82989 | 101.8712 | 104.8302 | 0.2838 | 0.34228 | 0.25132 | 0.25847 | 0.74164 | 0.75339 | 0.26773 | 0.3229 | 0.50713 | 0.65074 | 0.45152 | 0.45126 | 0.16564 | 0.096534 | 295.0019 | 264.0336
2013-04-30 | 85 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 20284.0743 | 19 | 55513.0586 | 17 | 2 | 5 | 350.5642 | 67.7977 | 180 | 2.6676 | 17 | 1250 | 66423.1377 | 9689.7975 | 308.0442 | 10.0466 | 13.4832 | 37 | 28.3814 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 8.6186 | 180 | 3.4367 | 12.6502 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0614 | 427.0971 | 1027.451 |  | 600.3539 | 9701.2047 | 2313.0441 | 845.1698 | 0.16699 | 18.1202 | 18.8327 | 0.02 | 0.05 | 30 | 165 | 453 | 623.5642 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 439.434 | 21.8141 | 1.111 | 1.0111 | 127.3539 | 473 | 438 | 451.1859 | 172.3783 | 0.2189 | 0.027 | 1.06 | 8.8533 | 8.8533 | 623.5642 | 600.3539 | 1.111 | 1.1049 | 2.245 | 1.9806 | 623.5642 | 600.3539 | 12.7652 | 1.111 | 1.1049 | 298.15 | 1.4952 | 1.3191 | 623.5642 | 6.4018 | 1.111 | 298.15 | 0.74984 | 0.66152 | 2.313 | 2.8374 | 18.8327 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.07094 | 0.07094 | 12.7652 | 435 | 451.1859 | 1.0621 | 1.0672 | 298.15 | 0.32844 | 0.4021 | 0.74101 | 453 | 2816.5993 | 6.5855 | 0.63562 | 0.67443 | 21.47 | 118.8638 | 0.40234 | 0.07636 | 0.07636 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 86.2524 | 42.1304 | 0.14667 | 0.26316 | 0.30549 | 86.2524 | 56.5133 | 0.19459 | 0.27133 | 0.31498 | 4.2952 | 4.0354 | 0.60207 | 0.31347 | 0.63869 | 0.67882 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 55.7548 | 0.20072 | 46.7947 | 0.16846 | 7.2547 | 0.026117 | 0.091831 | 7.3921 | 0.026612 | 0.093571 | 0.061882 | 0.058138 | 222.7739 | 209.2955 | 0.0057769 | 0.0030078 | 20.7967 | 10.8281 | 0.012662 | 0.0098965 | 45.5842 | 35.6275 | 6.6083 | 6.8727 | 2.313 | 2.3101 | 1.0931 | 0.91696 | 0.56468 | 0.60349 | 0.63562 | 0.67443 | 0.26316 | 0.30549 | 19.167 | 2313.0441 | 2837.3518 | 0.74101 | 0.78626 | 86.2524 | 100.1295 | 0.27694 | 0.33971 | 0.23818 | 0.25272 | 0.76019 | 0.63145 | 0.26126 | 0.32048 | 0.48398 | 0.65814 | 0.45297 | 0.41402 | 0.16846 | 0.093571 | 289.1548 | 255.751
2013-05-07 | 89 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 19145.5522 | 19 | 51666.2044 | 17 | 2 | 5 | 355.4989 | 84.1574 | 180 | 3.3504 | 17 | 1250 | 62559.7813 | 8891.0917 | 322.0694 | 10.8652 | 13.7103 | 37 | 28.4575 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 8.5425 | 180 | 2.8451 | 12.644 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0595 | 418.5884 | 1006.9819 |  | 588.3935 | 9503.2854 | 2152.7585 | 797.7313 | 0.15762 | 18.9453 | 23.3771 | 0.02 | 0.05 | 30 | 165 | 453 | 628.4989 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 551.9102 | 27.411 | 1.1124 | 1.0127 | 115.3935 | 473 | 438 | 445.589 | 182.9099 | 0.2189 | 0.027 | 1.06 | 8.3564 | 8.3564 | 628.4989 | 588.3935 | 1.1124 | 1.1018 | 2.3016 | 1.8482 | 628.4989 | 588.3935 | 12.759 | 1.1124 | 1.1018 | 298.15 | 1.5329 | 1.2309 | 628.4989 | 6.3986 | 1.1124 | 298.15 | 0.76875 | 0.61729 | 2.1528 | 2.6394 | 23.3771 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.088059 | 0.088059 | 12.759 | 435 | 445.589 | 1.0626 | 1.0658 | 298.15 | 0.32841 | 0.3759 | 0.93067 | 453 | 2816.5993 | 6.5855 | 0.79831 | 0.61151 | 21.47 | 119.1823 | 0.4034 | 0.076405 | 0.076405 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 90.1794 | 45.5566 | 0.15809 | 0.27717 | 0.32018 | 90.1794 | 57.4637 | 0.19776 | 0.28425 | 0.32836 | 3.902 | 3.8688 | 0.49424 | 0.33153 | 0.80032 | 0.61463 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 56.2015 | 0.20233 | 48.314 | 0.17393 | 7.031 | 0.025312 | 0.089 | 7.1257 | 0.025653 | 0.090199 | 0.056216 | 0.055737 | 202.377 | 200.6549 | 0.0047423 | 0.003181 | 17.0721 | 11.4516 | 0.013023 | 0.0096325 | 46.8822 | 34.6769 | 6.0547 | 6.5082 | 2.1528 | 1.7289 | 1.157 | 0.85498 | 0.71025 | 0.52346 | 0.79831 | 0.61151 | 0.27717 | 0.32018 | 19.1576 | 2152.7585 | 2639.4326 | 0.93067 | 0.71291 | 90.1794 | 104.1734 | 0.27308 | 0.33481 | 0.31688 | 0.24274 | 0.7406 | 0.47567 | 0.25762 | 0.31586 | 0.58967 | 0.61224 | 0.52359 | 0.3472 | 0.17393 | 0.090199 | 266.3314 | 246.7835
2013-05-16 | 97 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 20302.7447 | 19 | 56903.2917 | 17 | 2 | 5 | 356.5238 | 75.1866 | 180 | 2.9591 | 17 | 1250 | 69771.7278 | 10242.2499 | 343.3499 | 12.3012 | 15.6341 | 37 | 29.0084 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 7.9916 | 180 | 3.3329 | 12.6503 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0615 | 427.2366 | 1027.7865 |  | 600.5499 | 9704.4503 | 2370.9705 | 845.9477 | 0.16714 | 20.1971 | 20.8852 | 0.02 | 0.05 | 30 | 165 | 453 | 629.5238 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 487.447 | 24.1973 | 1.1126 | 1.0124 | 127.5499 | 473 | 438 | 448.8027 | 180.7211 | 0.2189 | 0.027 | 1.06 | 8.8615 | 8.8615 | 629.5238 | 600.5499 | 1.1126 | 1.105 | 2.3148 | 1.9828 | 629.5238 | 600.5499 | 12.7653 | 1.1126 | 1.105 | 298.15 | 1.5417 | 1.3205 | 629.5238 | 6.4018 | 1.1126 | 298.15 | 0.77316 | 0.66225 | 2.371 | 2.8406 | 20.8852 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.078672 | 0.078672 | 12.7653 | 435 | 448.8027 | 1.0623 | 1.0666 | 298.15 | 0.3285 | 0.39094 | 0.82197 | 453 | 2816.5993 | 6.5855 | 0.70506 | 0.67644 | 21.47 | 121.4876 | 0.41108 | 0.076731 | 0.076731 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 96.138 | 51.5665 | 0.17811 | 0.29929 | 0.33547 | 96.138 | 65.515 | 0.22459 | 0.30813 | 0.34538 | 4.1756 | 4.0381 | 0.5868 | 0.33182 | 0.70917 | 0.68161 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 54.0178 | 0.19446 | 46.7714 | 0.16838 | 7.4145 | 0.026692 | 0.093855 | 7.4936 | 0.026977 | 0.094855 | 0.060158 | 0.058177 | 216.5704 | 209.4358 | 0.0056304 | 0.0031839 | 20.2694 | 11.4619 | 0.013179 | 0.010171 | 47.4441 | 36.6139 | 6.5466 | 6.8787 | 2.371 | 2.1825 | 1.1507 | 0.92959 | 0.62639 | 0.59777 | 0.70506 | 0.67644 | 0.29929 | 0.33547 | 19.1671 | 2370.9705 | 2840.5974 | 0.82197 | 0.7886 | 96.138 | 107.759 | 0.28361 | 0.33979 | 0.26396 | 0.25324 | 0.76496 | 0.68364 | 0.26756 | 0.32056 | 0.51632 | 0.64304 | 0.49594 | 0.42449 | 0.16838 | 0.094855 | 284.2839 | 257.5116
2013-05-20 | 99 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 25958.4608 | 19 | 69844.16 | 17 | 2 | 5 | 369.9283 | 93.194 | 180 | 3.7216 | 17 | 1250 | 70616.9825 | 10373.8987 | 295.35 | 11.7807 | 15.8721 | 37 | 29.3103 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 7.6897 | 180 | 4.0914 | 12.681 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0716 | 469.3808 | 1129.1712 |  | 659.7904 | 10687.6327 | 2910.1733 | 1081.6025 | 0.2137 | 17.3735 | 25.8872 | 0.02 | 0.05 | 30 | 165 | 453 | 642.9283 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 613.0599 | 30.3591 | 1.1162 | 1.0155 | 186.7904 | 473 | 438 | 442.6409 | 200.2874 | 0.2189 | 0.027 | 1.06 | 11.33 | 11.33 | 642.9283 | 659.7904 | 1.1162 | 1.1207 | 2.4807 | 2.6876 | 642.9283 | 659.7904 | 12.7963 | 1.1162 | 1.1207 | 298.15 | 1.6521 | 1.7899 | 642.9283 | 6.4174 | 1.1162 | 298.15 | 0.82855 | 0.89765 | 2.9102 | 3.8238 | 25.8872 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.097514 | 0.097514 | 12.7963 | 435 | 442.6409 | 1.0628 | 1.0651 | 298.15 | 0.32944 | 0.36355 | 1.0338 | 453 | 2816.5993 | 6.5855 | 0.88676 | 0.9962 | 21.47 | 122.7515 | 0.41529 | 0.07691 | 0.07691 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 82.698 | 49.3878 | 0.17085 | 0.25627 | 0.46694 | 82.698 | 66.511 | 0.22791 | 0.2656 | 0.48394 | 5.9391 | 4.8186 | 0.53345 | 0.52769 | 0.89153 | 1.0087 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 55.409 | 0.19947 | 41.3907 | 0.14901 | 8.6862 | 0.03127 | 0.10995 | 9.4057 | 0.033861 | 0.11906 | 0.085565 | 0.069422 | 308.0346 | 249.9189 | 0.0051185 | 0.0050633 | 18.4266 | 18.2277 | 0.014336 | 0.015361 | 51.6104 | 55.2991 | 8.8493 | 8.6424 | 2.9102 | 4.2077 | 1.2886 | 1.4264 | 0.78924 | 0.89869 | 0.88676 | 0.9962 | 0.25627 | 0.46694 | 19.2137 | 2910.1733 | 3823.7799 | 1.0338 | 1.1614 | 82.698 | 150.6848 | 0.27227 | 0.35774 | 0.25977 | 0.29184 | 0.76552 | 1.0885 | 0.25686 | 0.33749 | 0.59669 | 0.63005 | 0.46872 | 0.28899 | 0.14901 | 0.11906 | 378.0717 | 323.4457
2013-05-21 | 100 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 23694.5256 | 19 | 56785.0364 | 17 | 2 | 5 | 350.8033 | 73.5585 | 180 | 2.8813 | 17 | 1250 | 70934.9774 | 10911.6329 | 300.528 | 11.7521 | 15.5398 | 37 | 28.6283 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 8.3717 | 180 | 3.7877 | 12.6687 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0675 | 452.5354 | 1088.6468 |  | 636.1114 | 10294.0731 | 2366.0432 | 987.2719 | 0.19507 | 17.6781 | 20.4329 | 0.02 | 0.05 | 30 | 165 | 453 | 623.8033 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 474.6301 | 23.5268 | 1.1111 | 1.0114 | 163.1114 | 473 | 438 | 449.4732 | 174.3301 | 0.2189 | 0.027 | 1.06 | 10.3419 | 10.3419 | 623.8033 | 636.1114 | 1.1111 | 1.1144 | 2.2511 | 2.3964 | 623.8033 | 636.1114 | 12.7839 | 1.1111 | 1.1144 | 298.15 | 1.4992 | 1.596 | 623.8033 | 6.4112 | 1.1111 | 298.15 | 0.75187 | 0.8004 | 2.366 | 3.4302 | 20.4329 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.076968 | 0.076968 | 12.7839 | 435 | 449.4732 | 1.0623 | 1.0668 | 298.15 | 0.32896 | 0.39465 | 0.80036 | 453 | 2816.5993 | 6.5855 | 0.68653 | 0.86511 | 21.47 | 119.897 | 0.40578 | 0.076506 | 0.076506 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 84.1478 | 49.2682 | 0.17045 | 0.26069 | 0.40816 | 84.1478 | 65.1201 | 0.22327 | 0.26948 | 0.42192 | 5.7247 | 4.5152 | 0.56071 | 0.41321 | 0.69036 | 0.87391 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 63.5328 | 0.22872 | 43.2124 | 0.15556 | 8.1078 | 0.029188 | 0.10263 | 8.6369 | 0.031093 | 0.10933 | 0.082476 | 0.065051 | 296.9136 | 234.1838 | 0.0053801 | 0.0039648 | 19.3682 | 14.2733 | 0.012717 | 0.012782 | 45.7821 | 46.0136 | 8.0908 | 7.9455 | 2.366 | 3.7102 | 1.1046 | 1.2014 | 0.60956 | 0.78814 | 0.68653 | 0.86511 | 0.26069 | 0.40816 | 19.1951 | 2366.0432 | 3430.2203 | 0.80036 | 1.0086 | 84.1478 | 131.7471 | 0.24251 | 0.35158 | 0.2203 | 0.2776 | 0.80159 | 0.78786 | 0.22878 | 0.33168 | 0.52087 | 0.65604 | 0.4718 | 0.37973 | 0.15556 | 0.10933 | 362.064 | 294.4707
2013-05-22 | 101 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 24500.4747 | 19 | 55857.0833 | 17 | 2 | 5 | 347.9048 | 71.6491 | 180 | 2.8114 | 17 | 1250 | 71067.2316 | 10561.9085 | 267.3286 | 11.6795 | 15.7842 | 37 | 28.4749 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 8.5251 | 180 | 4.1046 | 12.6731 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0689 | 458.536 | 1103.0823 |  | 644.5463 | 10434.1783 | 2327.3785 | 1020.8531 | 0.2017 | 15.7252 | 19.9025 | 0.02 | 0.05 | 30 | 165 | 453 | 620.9048 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 463.1137 | 22.948 | 1.1103 | 1.0109 | 171.5463 | 473 | 438 | 450.052 | 170.8528 | 0.2189 | 0.027 | 1.06 | 10.6936 | 10.6936 | 620.9048 | 644.5463 | 1.1103 | 1.1166 | 2.2181 | 2.4987 | 620.9048 | 644.5463 | 12.7883 | 1.1103 | 1.1166 | 298.15 | 1.4773 | 1.6641 | 620.9048 | 6.4134 | 1.1103 | 298.15 | 0.74085 | 0.83457 | 2.3274 | 3.5703 | 19.9025 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.07497 | 0.07497 | 12.7883 | 435 | 450.052 | 1.0622 | 1.0669 | 298.15 | 0.32906 | 0.3975 | 0.78094 | 453 | 2816.5993 | 6.5855 | 0.66987 | 0.90953 | 21.47 | 119.2551 | 0.40364 | 0.076415 | 0.076415 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 74.852 | 48.9645 | 0.16944 | 0.23174 | 0.4002 | 74.852 | 66.1429 | 0.22668 | 0.24022 | 0.41483 | 6.1481 | 4.6246 | 0.55331 | 0.43209 | 0.67329 | 0.91911 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 66.9699 | 0.24109 | 42.5233 | 0.15308 | 8.1223 | 0.02924 | 0.10281 | 8.8491 | 0.031857 | 0.11201 | 0.088576 | 0.066626 | 318.8737 | 239.8553 | 0.0053091 | 0.0041459 | 19.1126 | 14.9252 | 0.012469 | 0.013385 | 44.8883 | 48.1856 | 8.4755 | 8.1949 | 2.3274 | 4.1083 | 1.0798 | 1.2666 | 0.5949 | 0.83456 | 0.66987 | 0.90953 | 0.23174 | 0.4002 | 19.2017 | 2327.3785 | 3570.3254 | 0.78094 | 1.0603 | 74.852 | 129.2634 | 0.2307 | 0.35391 | 0.20789 | 0.28227 | 0.77446 | 0.88458 | 0.21764 | 0.33387 | 0.51811 | 0.65887 | 0.44001 | 0.34595 | 0.15308 | 0.11201 | 382.8746 | 302.9661
2013-05-23 | 102 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 25515.2191 | 19 | 58046.8358 | 17 | 2 | 5 | 349.3373 | 72.8107 | 180 | 2.8187 | 17 | 1250 | 69211.7046 | 9950.7915 | 275.0532 | 11.8517 | 15.9527 | 37 | 28.8203 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 8.1797 | 180 | 4.101 | 12.6786 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0708 | 466.0853 | 1121.2433 |  | 655.158 | 10610.5802 | 2418.6182 | 1063.1341 | 0.21006 | 16.1796 | 20.2252 | 0.02 | 0.05 | 30 | 165 | 453 | 622.3373 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 464.3231 | 22.9979 | 1.1107 | 1.0111 | 182.158 | 473 | 438 | 450.0021 | 172.3353 | 0.2189 | 0.027 | 1.06 | 11.1365 | 11.1365 | 622.3373 | 655.158 | 1.1107 | 1.1195 | 2.2358 | 2.6297 | 622.3373 | 655.158 | 12.7939 | 1.1107 | 1.1195 | 298.15 | 1.489 | 1.7514 | 622.3373 | 6.4162 | 1.1107 | 298.15 | 0.74674 | 0.8783 | 2.4186 | 3.7467 | 20.2252 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.076186 | 0.076186 | 12.7939 | 435 | 450.0021 | 1.0622 | 1.0669 | 298.15 | 0.32921 | 0.39743 | 0.78298 | 453 | 2816.5993 | 6.5855 | 0.67162 | 0.96654 | 21.47 | 120.7004 | 0.40846 | 0.07662 | 0.07662 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 77.0149 | 49.685 | 0.17184 | 0.23881 | 0.4406 | 77.0149 | 66.8481 | 0.22903 | 0.24751 | 0.45667 | 6.4822 | 4.7601 | 0.56437 | 0.46356 | 0.67548 | 0.97777 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 66.9767 | 0.24112 | 41.7207 | 0.15019 | 8.4257 | 0.030332 | 0.10665 | 9.2277 | 0.03322 | 0.11681 | 0.093388 | 0.068579 | 336.1983 | 246.8859 | 0.0054152 | 0.0044479 | 19.4948 | 16.0123 | 0.012625 | 0.014266 | 45.4484 | 51.3587 | 8.9008 | 8.5069 | 2.4186 | 4.4939 | 1.0916 | 1.3539 | 0.59543 | 0.89036 | 0.67162 | 0.96654 | 0.23881 | 0.4406 | 19.2101 | 2418.6182 | 3746.7273 | 0.78298 | 1.1268 | 77.0149 | 142.094 | 0.23021 | 0.35662 | 0.20016 | 0.28806 | 0.74921 | 0.95976 | 0.21718 | 0.33644 | 0.51339 | 0.65762 | 0.45585 | 0.35557 | 0.15019 | 0.11681 | 401.1415 | 314.2569
2013-05-31 | 107 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 24656.8137 | 19 | 67442.8844 | 17 | 2 | 5 | 312.1031 | 44.4367 | 180 | 1.8638 | 17 | 1250 | 6067.4639 | 267.9159 | 57.511 | 15.7917 | 17.3284 | 37 | 26.3647 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 10.6353 | 180 | 1.5368 | 12.674 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0692 | 459.6995 | 1105.8813 |  | 646.1818 | 10461.3561 | 2810.1202 | 1027.3672 | 0.20299 | 3.383 | 12.3435 | 0.02 | 0.05 | 30 | 165 | 453 | 585.1031 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 307.0224 | 15.2124 | 1.1009 | 1.0047 | 173.1818 | 473 | 438 | 457.7876 | 127.3155 | 0.2189 | 0.027 | 1.06 | 10.7619 | 10.7619 | 585.1031 | 646.1818 | 1.1009 | 1.1171 | 1.8169 | 2.5187 | 585.1031 | 646.1818 | 12.7892 | 1.1009 | 1.1171 | 298.15 | 1.21 | 1.6775 | 585.1031 | 6.4138 | 1.1009 | 298.15 | 0.60684 | 0.84126 | 2.8101 | 3.5975 | 12.3435 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.046496 | 0.046496 | 12.7892 | 435 | 457.7876 | 1.0616 | 1.0688 | 298.15 | 0.3289 | 0.4345 | 0.51772 | 453 | 2816.5993 | 6.5855 | 0.44409 | 0.91046 | 21.47 | 110.4238 | 0.37422 | 0.075166 | 0.075166 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 16.1031 | 66.1743 | 0.22678 | 0.051681 | 1.015 | 16.1031 | 72.6058 | 0.24821 | 0.052364 | 1.0284 | 6.1349 | 4.6456 | 0.48355 | 0.37901 | 0.43848 | 0.91757 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 57.8722 | 0.20834 | 42.3951 | 0.15262 | 2.0384 | 0.0073382 | 0.025802 | 9.4659 | 0.034077 | 0.11982 | 0.088385 | 0.06693 | 318.1854 | 240.9465 | 0.0046397 | 0.0036367 | 16.7029 | 13.092 | 0.009324 | 0.012666 | 33.5664 | 45.5989 | 8.945 | 8.2431 | 2.8101 | 4.9875 | 0.77555 | 1.243 | 0.39759 | 0.86396 | 0.44409 | 0.91046 | 0.051681 | 1.015 | 19.203 | 2810.1202 | 3597.5032 | 0.51772 | 1.0614 | 16.1031 | 316.2517 | 0.27679 | 0.35434 | 0.13695 | 0.28078 | 0.2301 | 0.15892 | 0.26112 | 0.33428 | 0.45122 | 0.69508 | 1.1148 | 0.11638 | 0.15262 | 0.11982 | 368.4547 | 299.6373
2013-06-10 | 108 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 20195.1537 | 19 | 56293.1208 | 17 | 2 | 5 | 332.8034 | 64.5678 | 180 | 2.502 | 17 | 1250 | 71333.6062 | 9653.5513 | 281.215 | 10.837 | 14.3782 | 37 | 28.4275 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 8.5725 | 180 | 3.5412 | 12.6497 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0613 | 426.4329 | 1025.8531 |  | 599.4202 | 9685.7468 | 2345.5467 | 841.4647 | 0.16626 | 16.5421 | 17.9355 | 0.02 | 0.05 | 30 | 165 | 453 | 605.8034 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 412.147 | 20.4603 | 1.1063 | 1.0083 | 126.4202 | 473 | 438 | 452.5397 | 153.2637 | 0.2189 | 0.027 | 1.06 | 8.8145 | 8.8145 | 605.8034 | 599.4202 | 1.1063 | 1.1047 | 2.0415 | 1.9701 | 605.8034 | 599.4202 | 12.7647 | 1.1063 | 1.1047 | 298.15 | 1.3596 | 1.3121 | 605.8034 | 6.4015 | 1.1063 | 298.15 | 0.68186 | 0.65802 | 2.3455 | 2.8219 | 17.9355 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.067561 | 0.067561 | 12.7647 | 435 | 452.5397 | 1.062 | 1.0675 | 298.15 | 0.3284 | 0.40849 | 0.69499 | 453 | 2816.5993 | 6.5855 | 0.59615 | 0.66663 | 21.47 | 119.0566 | 0.40298 | 0.076387 | 0.076387 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 78.7402 | 45.4386 | 0.15769 | 0.24195 | 0.29415 | 78.7402 | 60.2587 | 0.20707 | 0.24964 | 0.30349 | 4.4274 | 4.0225 | 0.50266 | 0.30455 | 0.59876 | 0.6709 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 55.9938 | 0.20158 | 46.9063 | 0.16886 | 7.0961 | 0.025546 | 0.089823 | 7.3261 | 0.026374 | 0.092736 | 0.063786 | 0.057952 | 229.6302 | 208.6268 | 0.0048231 | 0.0029222 | 17.3631 | 10.5198 | 0.011209 | 0.0097099 | 40.3507 | 34.9556 | 6.773 | 6.8444 | 2.3455 | 2.6769 | 0.95116 | 0.90362 | 0.52859 | 0.59907 | 0.59615 | 0.66663 | 0.24195 | 0.29415 | 19.1663 | 2345.5467 | 2821.894 | 0.69499 | 0.77716 | 78.7402 | 95.7263 | 0.28207 | 0.33935 | 0.22437 | 0.2509 | 0.70521 | 0.67029 | 0.2661 | 0.32014 | 0.51257 | 0.66297 | 0.44125 | 0.40586 | 0.16886 | 0.092736 | 287.344 | 254.1021
2013-06-11 | 109 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 20796.1177 | 19 | 58228.4422 | 17 | 2 | 5 | 346.8226 | 73.537 | 180 | 2.8549 | 17 | 1250 | 88723.4318 | 12305.5011 | 368.7495 | 11.779 | 15.0559 | 37 | 29.0381 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 7.9619 | 180 | 3.2769 | 12.653 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0623 | 430.9212 | 1036.6504 |  | 605.7292 | 9790.2176 | 2426.1851 | 866.5049 | 0.17121 | 21.6911 | 20.427 | 0.02 | 0.05 | 30 | 165 | 453 | 619.8226 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 470.2907 | 23.3407 | 1.1101 | 1.0108 | 132.7292 | 473 | 438 | 449.6593 | 170.1633 | 0.2189 | 0.027 | 1.06 | 9.0768 | 9.0768 | 619.8226 | 605.7292 | 1.1101 | 1.1063 | 2.2021 | 2.0412 | 619.8226 | 605.7292 | 12.768 | 1.1101 | 1.1063 | 298.15 | 1.4666 | 1.3594 | 619.8226 | 6.4032 | 1.1101 | 298.15 | 0.73549 | 0.68176 | 2.4262 | 2.9264 | 20.427 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.076946 | 0.076946 | 12.768 | 435 | 449.6593 | 1.0623 | 1.0668 | 298.15 | 0.32855 | 0.39503 | 0.79304 | 453 | 2816.5993 | 6.5855 | 0.68025 | 0.70242 | 21.47 | 121.612 | 0.4115 | 0.076748 | 0.076748 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 103.2499 | 49.381 | 0.17083 | 0.31995 | 0.35951 | 103.2499 | 63.0952 | 0.21652 | 0.32928 | 0.36999 | 4.4485 | 4.1092 | 0.53472 | 0.33894 | 0.68486 | 0.70819 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 54.737 | 0.19705 | 46.1732 | 0.16622 | 7.6008 | 0.027363 | 0.096213 | 7.6981 | 0.027713 | 0.097444 | 0.06409 | 0.059202 | 230.7249 | 213.1262 | 0.0051307 | 0.0032521 | 18.4706 | 11.7076 | 0.012396 | 0.010477 | 44.6244 | 37.7184 | 6.8747 | 7.0356 | 2.4262 | 2.6062 | 1.0716 | 0.96441 | 0.6033 | 0.62548 | 0.68025 | 0.70242 | 0.31995 | 0.35951 | 19.1712 | 2426.1851 | 2926.3648 | 0.79304 | 0.81889 | 103.2499 | 116.0169 | 0.28333 | 0.34174 | 0.24864 | 0.25674 | 0.72275 | 0.6685 | 0.2673 | 0.3224 | 0.53013 | 0.64856 | 0.51181 | 0.47034 | 0.16622 | 0.097444 | 293.8199 | 262.5523
2013-06-12 | 110 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 21715.2896 | 19 | 61745.2939 | 17 | 2 | 5 | 358.2008 | 81.7731 | 180 | 3.2454 | 17 | 1250 | 74725.6351 | 10654.011 | 330.1583 | 9.9779 | 13.7337 | 37 | 27.6847 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 9.3153 | 180 | 3.7558 | 12.658 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.064 | 437.7815 | 1053.154 |  | 615.3725 | 9950.0053 | 2572.7206 | 904.8037 | 0.17877 | 19.4211 | 22.7148 | 0.02 | 0.05 | 30 | 165 | 453 | 631.2008 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 534.6042 | 26.5222 | 1.1131 | 1.013 | 142.3725 | 473 | 438 | 446.4778 | 184.723 | 0.2189 | 0.027 | 1.06 | 9.478 | 9.478 | 631.2008 | 615.3725 | 1.1131 | 1.1089 | 2.3361 | 2.1516 | 631.2008 | 615.3725 | 12.7731 | 1.1131 | 1.1089 | 298.15 | 1.5558 | 1.433 | 631.2008 | 6.4057 | 1.1131 | 298.15 | 0.78024 | 0.71865 | 2.5727 | 3.0862 | 22.7148 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.085564 | 0.085564 | 12.7731 | 435 | 446.4778 | 1.0625 | 1.066 | 298.15 | 0.32875 | 0.38041 | 0.90149 | 453 | 2816.5993 | 6.5855 | 0.77327 | 0.75581 | 21.47 | 115.9481 | 0.39263 | 0.075947 | 0.075947 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 92.4443 | 41.843 | 0.14571 | 0.28187 | 0.31905 | 92.4443 | 57.5616 | 0.19809 | 0.29145 | 0.32989 | 4.5692 | 4.2402 | 0.53935 | 0.38235 | 0.77733 | 0.76113 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 53.1156 | 0.19122 | 45.1398 | 0.1625 | 7.7158 | 0.027777 | 0.097668 | 7.8352 | 0.028207 | 0.099179 | 0.065829 | 0.061088 | 236.9833 | 219.9184 | 0.0051751 | 0.0036686 | 18.6303 | 13.2071 | 0.013308 | 0.011469 | 47.909 | 41.2891 | 7.1419 | 7.3263 | 2.5727 | 2.7264 | 1.1754 | 1.0526 | 0.68771 | 0.67024 | 0.77327 | 0.75581 | 0.28187 | 0.31905 | 19.1788 | 2572.7206 | 3086.1524 | 0.90149 | 0.88113 | 92.4443 | 104.6381 | 0.28773 | 0.34515 | 0.2707 | 0.26459 | 0.74297 | 0.64062 | 0.27144 | 0.32561 | 0.56045 | 0.63676 | 0.42213 | 0.36452 | 0.1625 | 0.099179 | 303.5227 | 274.4145
2013-06-13 | 111 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 28005.6154 | 19 | 78473.4692 | 17 | 2 | 5 | 356.8602 | 64.986 | 180 | 2.5516 | 17 | 1250 | 75399.8547 | 10993.3445 | 370.7611 | 11.4649 | 14.7952 | 37 | 28.0328 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 8.9672 | 180 | 3.3304 | 12.6922 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0753 | 484.5851 | 1165.7476 |  | 681.1625 | 11043.5075 | 3269.7279 | 1166.9006 | 0.23056 | 21.8095 | 18.0517 | 0.02 | 0.05 | 30 | 165 | 453 | 629.8602 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 420.3171 | 20.7961 | 1.1127 | 1.0119 | 208.1625 | 473 | 438 | 452.2039 | 177.6563 | 0.2189 | 0.027 | 1.06 | 12.2235 | 12.2235 | 629.8602 | 681.1625 | 1.1127 | 1.1265 | 2.3265 | 2.9608 | 629.8602 | 681.1625 | 12.8076 | 1.1127 | 1.1265 | 298.15 | 1.5494 | 1.9719 | 629.8602 | 6.423 | 1.1127 | 298.15 | 0.77705 | 0.98891 | 3.2697 | 4.1797 | 18.0517 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.067998 | 0.067998 | 12.8076 | 435 | 452.2039 | 1.0621 | 1.0674 | 298.15 | 0.32951 | 0.40826 | 0.70877 | 453 | 2816.5993 | 6.5855 | 0.60796 | 1.1077 | 21.47 | 117.4047 | 0.39748 | 0.076153 | 0.076153 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 103.8131 | 48.0662 | 0.16645 | 0.32079 | 0.62776 | 103.8131 | 62.0041 | 0.21289 | 0.33033 | 0.64641 | 6.6273 | 5.083 | 0.67997 | 0.52393 | 0.61219 | 1.121 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 53.9323 | 0.19416 | 40.0046 | 0.14402 | 9.5242 | 0.034287 | 0.12056 | 10.2266 | 0.036816 | 0.12945 | 0.095479 | 0.073231 | 343.7256 | 263.6333 | 0.0065243 | 0.0050272 | 23.4875 | 18.0979 | 0.013271 | 0.016177 | 47.7755 | 58.2371 | 9.897 | 9.2627 | 3.2697 | 5.3488 | 1.1412 | 1.5636 | 0.53997 | 1.0397 | 0.60796 | 1.1077 | 0.32079 | 0.62776 | 19.2306 | 3269.7279 | 4179.6546 | 0.70877 | 1.2914 | 103.8131 | 203.1502 | 0.28354 | 0.36245 | 0.16511 | 0.30082 | 0.75977 | 0.56139 | 0.2675 | 0.34194 | 0.44262 | 0.66492 | 0.56672 | 0.52765 | 0.14402 | 0.12945 | 414.9887 | 339.9683
2013-06-14 | 112 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 21122.8965 | 19 | 57609.6964 | 17 | 2 | 5 | 347.8153 | 74.6593 | 180 | 2.9152 | 17 | 1250 | 87461.5905 | 12353.4702 | 367.758 | 11.3128 | 15.3109 | 37 | 28.3477 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 8.6523 | 180 | 3.9981 | 12.6548 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0629 | 433.3607 | 1042.5191 |  | 609.1584 | 9847.0244 | 2400.404 | 880.1207 | 0.1739 | 21.6328 | 20.7387 | 0.02 | 0.05 | 30 | 165 | 453 | 620.8153 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 480.2178 | 23.8301 | 1.1103 | 1.011 | 136.1584 | 473 | 438 | 449.1699 | 171.6454 | 0.2189 | 0.027 | 1.06 | 9.2194 | 9.2194 | 620.8153 | 609.1584 | 1.1103 | 1.1072 | 2.2139 | 2.0802 | 620.8153 | 609.1584 | 12.7698 | 1.1103 | 1.1072 | 298.15 | 1.4744 | 1.3854 | 620.8153 | 6.4041 | 1.1103 | 298.15 | 0.73943 | 0.6948 | 2.4004 | 2.9832 | 20.7387 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.07812 | 0.07812 | 12.7698 | 435 | 449.1699 | 1.0623 | 1.0667 | 298.15 | 0.32861 | 0.39279 | 0.80978 | 453 | 2816.5993 | 6.5855 | 0.69461 | 0.72084 | 21.47 | 118.7229 | 0.40187 | 0.07634 | 0.07634 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 102.9722 | 47.4298 | 0.16433 | 0.31776 | 0.29315 | 102.9722 | 64.1623 | 0.22008 | 0.32912 | 0.30363 | 4.6052 | 4.156 | 0.52935 | 0.34991 | 0.70084 | 0.7262 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 56.11 | 0.202 | 45.7943 | 0.16486 | 7.6814 | 0.027653 | 0.097233 | 7.5769 | 0.027277 | 0.09591 | 0.066346 | 0.059876 | 238.847 | 215.5533 | 0.0050791 | 0.0033574 | 18.2848 | 12.0868 | 0.012499 | 0.010761 | 44.9951 | 38.7409 | 7.0056 | 7.1392 | 2.4004 | 2.7183 | 1.0816 | 0.99264 | 0.61649 | 0.64272 | 0.69461 | 0.72084 | 0.31776 | 0.29315 | 19.1739 | 2400.404 | 2983.1716 | 0.80978 | 0.84037 | 102.9722 | 94.997 | 0.27599 | 0.34299 | 0.24997 | 0.25941 | 0.73603 | 0.81774 | 0.26036 | 0.32357 | 0.53803 | 0.64749 | 0.40668 | 0.45747 | 0.16486 | 0.09591 | 302.127 | 266.3809
2013-06-17 | 113 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 20830.2267 | 19 | 56218.9392 | 17 | 2 | 5 | 338.5868 | 66.5647 | 180 | 2.5893 | 17 | 1250 | 70030.9521 | 9930.2027 | 320.8073 | 11.4155 | 14.9305 | 37 | 27.8797 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 9.1203 | 180 | 3.515 | 12.6532 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0624 | 431.1758 | 1037.263 |  | 606.0872 | 9796.1471 | 2342.4558 | 867.9261 | 0.17149 | 18.871 | 18.4902 | 0.02 | 0.05 | 30 | 165 | 453 | 611.5868 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 426.5372 | 21.1689 | 1.1079 | 1.0092 | 133.0872 | 473 | 438 | 451.8311 | 159.7557 | 0.2189 | 0.027 | 1.06 | 9.0917 | 9.0917 | 611.5868 | 606.0872 | 1.1079 | 1.1064 | 2.1076 | 2.0453 | 611.5868 | 606.0872 | 12.7682 | 1.1079 | 1.1064 | 298.15 | 1.4036 | 1.3621 | 611.5868 | 6.4033 | 1.1079 | 298.15 | 0.70392 | 0.68312 | 2.3425 | 2.9323 | 18.4902 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.06965 | 0.06965 | 12.7682 | 435 | 451.8311 | 1.0621 | 1.0673 | 298.15 | 0.3285 | 0.40524 | 0.71926 | 453 | 2816.5993 | 6.5855 | 0.61696 | 0.70295 | 21.47 | 116.7641 | 0.39534 | 0.076063 | 0.076063 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 89.826 | 47.8596 | 0.16576 | 0.27745 | 0.31258 | 89.826 | 62.5701 | 0.21477 | 0.28616 | 0.32239 | 4.6417 | 4.1141 | 0.52782 | 0.32361 | 0.62027 | 0.70735 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 57.3663 | 0.20652 | 46.133 | 0.16608 | 7.4398 | 0.026783 | 0.094175 | 7.5677 | 0.027244 | 0.095793 | 0.066873 | 0.059272 | 240.7415 | 213.3802 | 0.0050644 | 0.003105 | 18.232 | 11.1781 | 0.011691 | 0.010255 | 42.0878 | 36.9189 | 6.9841 | 7.0464 | 2.3425 | 2.8073 | 0.99839 | 0.9569 | 0.54731 | 0.6333 | 0.61696 | 0.70295 | 0.27745 | 0.31258 | 19.1715 | 2342.4558 | 2932.2942 | 0.71926 | 0.8195 | 89.826 | 101.2 | 0.27311 | 0.34188 | 0.22514 | 0.25651 | 0.73891 | 0.5953 | 0.25765 | 0.32252 | 0.50907 | 0.66182 | 0.44467 | 0.4497 | 0.16608 | 0.095793 | 301.0613 | 261.4771
2013-06-18 | 114 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 20021.5722 | 19 | 57181.015 | 17 | 2 | 5 | 343.0172 | 69.4996 | 180 | 2.7604 | 17 | 1250 | 78095.9677 | 11457.5239 | 362.3238 | 11.4742 | 14.5872 | 37 | 27.8043 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 9.1957 | 180 | 3.1129 | 12.6488 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.061 | 425.1361 | 1022.7333 |  | 597.5973 | 9655.5716 | 2382.5423 | 834.2322 | 0.16483 | 21.3132 | 19.3054 | 0.02 | 0.05 | 30 | 165 | 453 | 616.0172 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 454.7137 | 22.5751 | 1.109 | 1.0101 | 124.5973 | 473 | 438 | 450.4249 | 165.5924 | 0.2189 | 0.027 | 1.06 | 8.7387 | 8.7387 | 616.0172 | 597.5973 | 1.109 | 1.1042 | 2.1575 | 1.9498 | 616.0172 | 597.5973 | 12.7638 | 1.109 | 1.1042 | 298.15 | 1.4369 | 1.2985 | 616.0172 | 6.4011 | 1.109 | 298.15 | 0.7206 | 0.65122 | 2.3825 | 2.7917 | 19.3054 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.072721 | 0.072721 | 12.7638 | 435 | 450.4249 | 1.0622 | 1.067 | 298.15 | 0.32842 | 0.39848 | 0.76677 | 453 | 2816.5993 | 6.5855 | 0.65772 | 0.65857 | 21.47 | 116.4484 | 0.39429 | 0.076018 | 0.076018 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 101.4507 | 48.1054 | 0.16658 | 0.31352 | 0.31696 | 101.4507 | 61.1334 | 0.20999 | 0.32223 | 0.32577 | 4.1987 | 3.9973 | 0.52346 | 0.31421 | 0.66098 | 0.66193 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 53.965 | 0.19427 | 47.1274 | 0.16966 | 7.3707 | 0.026534 | 0.0933 | 7.3583 | 0.02649 | 0.093143 | 0.060491 | 0.057588 | 217.7673 | 207.3184 | 0.0050227 | 0.0030149 | 18.0816 | 10.8536 | 0.012017 | 0.0097577 | 43.262 | 35.1276 | 6.5813 | 6.789 | 2.3825 | 2.3734 | 1.0384 | 0.90006 | 0.585 | 0.58585 | 0.65772 | 0.65857 | 0.31352 | 0.31696 | 19.1648 | 2382.5423 | 2791.7188 | 0.76677 | 0.76777 | 101.4507 | 102.5649 | 0.289 | 0.33863 | 0.24968 | 0.25001 | 0.76452 | 0.48562 | 0.27264 | 0.31946 | 0.52776 | 0.6509 | 0.48129 | 0.47668 | 0.16966 | 0.093143 | 279.1108 | 253.2996
2013-06-19 | 115 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 20641.557 | 19 | 57821.8372 | 17 | 2 | 5 | 350.4453 | 72.7738 | 180 | 2.9899 | 17 | 1250 | 78225.5353 | 11266.3209 | 348.6038 | 11.2464 | 14.323 | 37 | 28.1338 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 8.8662 | 180 | 3.0766 | 12.6522 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0621 | 429.7671 | 1033.874 |  | 604.1069 | 9763.349 | 2409.2432 | 860.0649 | 0.16993 | 20.5061 | 20.2149 | 0.02 | 0.05 | 30 | 165 | 453 | 623.4453 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 492.5159 | 24.4454 | 1.111 | 1.0115 | 131.1069 | 473 | 438 | 448.5546 | 174.8907 | 0.2189 | 0.027 | 1.06 | 9.0093 | 9.0093 | 623.4453 | 604.1069 | 1.111 | 1.1059 | 2.244 | 2.0228 | 623.4453 | 604.1069 | 12.7672 | 1.111 | 1.1059 | 298.15 | 1.4945 | 1.3472 | 623.4453 | 6.4028 | 1.111 | 298.15 | 0.74949 | 0.67563 | 2.4092 | 2.8995 | 20.2149 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.076147 | 0.076147 | 12.7672 | 435 | 448.5546 | 1.0623 | 1.0665 | 298.15 | 0.32855 | 0.38985 | 0.83052 | 453 | 2816.5993 | 6.5855 | 0.7124 | 0.69439 | 21.47 | 117.8277 | 0.39889 | 0.076213 | 0.076213 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 97.6091 | 47.1518 | 0.1634 | 0.30103 | 0.35532 | 97.6091 | 60.0277 | 0.2063 | 0.30931 | 0.3651 | 4.3561 | 4.087 | 0.52969 | 0.33912 | 0.71543 | 0.69892 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 54.4678 | 0.19608 | 46.3571 | 0.16689 | 7.5008 | 0.027003 | 0.094947 | 7.6437 | 0.027517 | 0.096755 | 0.062759 | 0.058882 | 225.931 | 211.9735 | 0.0050824 | 0.0032538 | 18.2966 | 11.7138 | 0.012579 | 0.010385 | 45.286 | 37.3845 | 6.7654 | 6.9865 | 2.4092 | 2.4602 | 1.1046 | 0.95736 | 0.63625 | 0.61825 | 0.7124 | 0.69439 | 0.30103 | 0.35532 | 19.1699 | 2409.2432 | 2899.4961 | 0.83052 | 0.80953 | 97.6091 | 115.2119 | 0.28346 | 0.34114 | 0.26233 | 0.2557 | 0.75051 | 0.50523 | 0.26742 | 0.32183 | 0.5457 | 0.64578 | 0.5117 | 0.42257 | 0.16689 | 0.096755 | 289.5136 | 261.0719
2013-06-20 | 116 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 20145.8411 | 19 | 57071.5308 | 17 | 2 | 5 | 372.3208 | 64.3208 | 180 | 2.9133 | 17 | 1250 | 64073.502 | 9570.8426 | 305.3186 | 11.8885 | 15.1024 | 37 | 27.946 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 9.054 | 180 | 3.2139 | 12.6495 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0612 | 426.0645 | 1024.9668 |  | 598.9023 | 9677.1744 | 2377.9805 | 839.41 | 0.16585 | 17.9599 | 17.8669 | 0.02 | 0.05 | 30 | 165 | 453 | 645.3208 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 479.9002 | 23.8243 | 1.1168 | 1.0149 | 125.9023 | 473 | 438 | 449.1757 | 196.1451 | 0.2189 | 0.027 | 1.06 | 8.793 | 8.793 | 645.3208 | 598.9023 | 1.1168 | 1.1045 | 2.5034 | 1.9643 | 645.3208 | 598.9023 | 12.7645 | 1.1168 | 1.1045 | 298.15 | 1.6673 | 1.3082 | 645.3208 | 6.4014 | 1.1168 | 298.15 | 0.83614 | 0.65609 | 2.378 | 2.8133 | 17.8669 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.067302 | 0.067302 | 12.7645 | 435 | 449.1757 | 1.0623 | 1.0667 | 298.15 | 0.32847 | 0.39266 | 0.80924 | 453 | 2816.5993 | 6.5855 | 0.69415 | 0.67018 | 21.47 | 117.0415 | 0.39627 | 0.076102 | 0.076102 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 85.4892 | 49.839 | 0.17236 | 0.26517 | 0.31987 | 85.4892 | 63.2895 | 0.21717 | 0.27275 | 0.32901 | 3.9116 | 4.0153 | 0.71197 | 0.31271 | 0.69636 | 0.67396 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 52.3012 | 0.18828 | 46.9687 | 0.16909 | 7.2635 | 0.026149 | 0.091943 | 7.4022 | 0.026648 | 0.093698 | 0.056354 | 0.057849 | 202.8746 | 208.2555 | 0.0068314 | 0.0030005 | 24.5929 | 10.8017 | 0.014271 | 0.0098209 | 51.3742 | 35.3554 | 6.2896 | 6.8286 | 2.378 | 1.759 | 1.2746 | 0.91559 | 0.62685 | 0.60288 | 0.69415 | 0.67018 | 0.26517 | 0.31987 | 19.1659 | 2377.9805 | 2813.3215 | 0.80924 | 0.7813 | 85.4892 | 103.125 | 0.28667 | 0.33915 | 0.26189 | 0.25284 | 0.77839 | 0.52263 | 0.27044 | 0.31995 | 0.46821 | 0.65846 | 0.47729 | 0.38201 | 0.16909 | 0.093698 | 278.8417 | 254.4125
2013-06-21 | 117 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 20883.3708 | 19 | 58624.7656 | 17 | 2 | 5 | 353.5647 | 68.9645 | 180 | 2.7237 | 17 | 1250 | 73437.7661 | 10992.4593 | 337.3324 | 11.8295 | 15.4061 | 37 | 28.4704 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 8.5296 | 180 | 3.5767 | 12.6535 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0625 | 431.5726 | 1038.2175 |  | 606.6449 | 9805.3856 | 2442.6986 | 870.1404 | 0.17192 | 19.8431 | 19.1568 | 0.02 | 0.05 | 30 | 165 | 453 | 626.5647 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 448.671 | 22.2669 | 1.1118 | 1.0116 | 133.6449 | 473 | 438 | 450.7331 | 175.8316 | 0.2189 | 0.027 | 1.06 | 9.1149 | 9.1149 | 626.5647 | 606.6449 | 1.1118 | 1.1066 | 2.2807 | 2.0516 | 626.5647 | 606.6449 | 12.7685 | 1.1118 | 1.1066 | 298.15 | 1.5189 | 1.3664 | 626.5647 | 6.4034 | 1.1118 | 298.15 | 0.76174 | 0.68523 | 2.4427 | 2.9415 | 19.1568 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.072161 | 0.072161 | 12.7685 | 435 | 450.7331 | 1.0622 | 1.0671 | 298.15 | 0.32854 | 0.40008 | 0.75658 | 453 | 2816.5993 | 6.5855 | 0.64898 | 0.70844 | 21.47 | 119.2364 | 0.40358 | 0.076412 | 0.076412 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 94.4531 | 49.5921 | 0.17153 | 0.29282 | 0.32305 | 94.4531 | 64.5609 | 0.22141 | 0.30214 | 0.33333 | 4.3915 | 4.1218 | 0.61357 | 0.33001 | 0.65324 | 0.71366 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 54.128 | 0.19486 | 46.0707 | 0.16585 | 7.5378 | 0.027136 | 0.095415 | 7.6172 | 0.027422 | 0.09642 | 0.063269 | 0.059382 | 227.7674 | 213.7756 | 0.0058872 | 0.0031665 | 21.1939 | 11.3993 | 0.012935 | 0.010399 | 46.5666 | 37.4373 | 6.8342 | 7.0633 | 2.4427 | 2.489 | 1.1188 | 0.96629 | 0.57682 | 0.63628 | 0.64898 | 0.70844 | 0.29282 | 0.32305 | 19.1719 | 2442.6986 | 2941.5327 | 0.75658 | 0.8259 | 94.4531 | 104.2048 | 0.28407 | 0.34208 | 0.23622 | 0.25786 | 0.78001 | 0.68792 | 0.26799 | 0.32272 | 0.48456 | 0.65848 | 0.45601 | 0.4512 | 0.16585 | 0.09642 | 295.528 | 262.6122
2013-06-23 | 118 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 24737.9312 | 19 | 69345.0161 | 17 | 2 | 5 | 288.8316 | 34.1946 | 180 | 1.4192 | 17 | 1250 | 43923.4935 | 5824.7838 | 291.4286 | 11.2972 | 13.9721 | 37 | 27.8502 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 9.1498 | 180 | 2.6749 | 12.6744 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0694 | 460.3032 | 1107.3335 |  | 647.0303 | 10475.4574 | 2889.3757 | 1030.7471 | 0.20366 | 17.1429 | 9.4985 | 0.02 | 0.05 | 30 | 165 | 453 | 561.8316 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 233.7818 | 11.5831 | 1.0948 | 1.0013 | 174.0303 | 473 | 438 | 461.4169 | 100.4147 | 0.2189 | 0.027 | 1.06 | 10.7973 | 10.7973 | 561.8316 | 647.0303 | 1.0948 | 1.1173 | 1.5721 | 2.5291 | 561.8316 | 647.0303 | 12.7896 | 1.0948 | 1.1173 | 298.15 | 1.047 | 1.6844 | 561.8316 | 6.414 | 1.0948 | 298.15 | 0.52508 | 0.84473 | 2.8894 | 3.6116 | 9.4985 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.03578 | 0.03578 | 12.7896 | 435 | 461.4169 | 1.0614 | 1.0696 | 298.15 | 0.32883 | 0.45231 | 0.39422 | 453 | 2816.5993 | 6.5855 | 0.33815 | 0.90992 | 21.47 | 116.6408 | 0.39493 | 0.076045 | 0.076045 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 81.6 | 47.3645 | 0.16411 | 0.25178 | 0.59691 | 81.6 | 58.5591 | 0.20141 | 0.25779 | 0.61118 | 6.3358 | 4.6565 | 0.41581 | 0.35796 | 0.33875 | 0.91877 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 57.682 | 0.20766 | 42.3293 | 0.15239 | 8.2229 | 0.029603 | 0.10409 | 9.2289 | 0.033224 | 0.11682 | 0.09128 | 0.067087 | 328.6078 | 241.5115 | 0.0039897 | 0.0034346 | 14.363 | 12.3647 | 0.0077201 | 0.012426 | 27.7925 | 44.7324 | 9.2252 | 8.2681 | 2.8894 | 5.5505 | 0.5947 | 1.2321 | 0.30237 | 0.87414 | 0.33815 | 0.90992 | 0.25178 | 0.59691 | 19.2037 | 2889.3757 | 3611.6046 | 0.39422 | 1.0608 | 81.6 | 193.4578 | 0.28366 | 0.35456 | 0.10394 | 0.27969 | 0.69105 | 0.39211 | 0.2676 | 0.33449 | 0.42102 | 0.70947 | 0.656 | 0.74456 | 0.15239 | 0.11682 | 370.7634 | 298.6085
2013-06-24 | 119 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 19627.7034 | 19 | 56633.3606 | 17 | 2 | 5 | 344.4236 | 76.8864 | 180 | 3.0839 | 17 | 1250 | 68920.9593 | 9969.412 | 331.2518 | 11.3679 | 14.4562 | 37 | 28.8233 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 8.1767 | 180 | 3.0884 | 12.6466 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0603 | 422.1928 | 1015.6528 |  | 593.46 | 9587.102 | 2359.7234 | 817.821 | 0.16159 | 19.4854 | 21.3573 | 0.02 | 0.05 | 30 | 165 | 453 | 617.4236 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 508.0044 | 25.2251 | 1.1094 | 1.0107 | 120.46 | 473 | 438 | 447.7749 | 169.6488 | 0.2189 | 0.027 | 1.06 | 8.5668 | 8.5668 | 617.4236 | 593.46 | 1.1094 | 1.1031 | 2.1733 | 1.9038 | 617.4236 | 593.46 | 12.7616 | 1.1094 | 1.1031 | 298.15 | 1.4474 | 1.268 | 617.4236 | 6.4 | 1.1094 | 298.15 | 0.72588 | 0.63588 | 2.3597 | 2.7232 | 21.3573 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.08045 | 0.08045 | 12.7616 | 435 | 447.7749 | 1.0624 | 1.0663 | 298.15 | 0.32843 | 0.38606 | 0.85664 | 453 | 2816.5993 | 6.5855 | 0.7348 | 0.63681 | 21.47 | 120.713 | 0.4085 | 0.076621 | 0.076621 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 92.7505 | 47.6603 | 0.1651 | 0.28636 | 0.32398 | 92.7505 | 60.5854 | 0.20816 | 0.29426 | 0.33292 | 4.0338 | 3.9397 | 0.46463 | 0.32555 | 0.73786 | 0.6409 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 53.3408 | 0.19203 | 47.6458 | 0.17152 | 7.1744 | 0.025828 | 0.090815 | 7.2712 | 0.026176 | 0.092041 | 0.058115 | 0.05676 | 209.215 | 204.335 | 0.0044582 | 0.0031236 | 16.0494 | 11.2451 | 0.012107 | 0.0097478 | 43.5848 | 35.0922 | 6.3935 | 6.663 | 2.3597 | 2.1791 | 1.0614 | 0.88191 | 0.65435 | 0.55636 | 0.7348 | 0.63681 | 0.28636 | 0.32398 | 19.1616 | 2359.7234 | 2723.2491 | 0.85664 | 0.7424 | 92.7505 | 104.9364 | 0.29198 | 0.33696 | 0.28453 | 0.24658 | 0.75378 | 0.57938 | 0.27545 | 0.31788 | 0.58477 | 0.63086 | 0.50876 | 0.38971 | 0.17152 | 0.092041 | 268.8492 | 250.6723
2013-06-25 | 120 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 20104.0153 | 19 | 57637.4811 | 17 | 2 | 5 | 328.3946 | 58.2251 | 180 | 2.3579 | 17 | 1250 | 52396.8454 | 7687.5438 | 269.9392 | 12.0512 | 15.072 | 37 | 28.0474 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 8.9526 | 180 | 3.0208 | 12.6492 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0611 | 425.752 | 1024.2151 |  | 598.4631 | 9669.9034 | 2401.5617 | 837.6673 | 0.16551 | 15.8788 | 16.1737 | 0.02 | 0.05 | 30 | 165 | 453 | 601.3946 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 388.4083 | 19.2826 | 1.1052 | 1.0075 | 125.4631 | 473 | 438 | 453.7174 | 147.6772 | 0.2189 | 0.027 | 1.06 | 8.7747 | 8.7747 | 601.3946 | 598.4631 | 1.1052 | 1.1044 | 1.992 | 1.9594 | 601.3946 | 598.4631 | 12.7642 | 1.1052 | 1.1044 | 298.15 | 1.3267 | 1.305 | 601.3946 | 6.4013 | 1.1052 | 298.15 | 0.66534 | 0.65445 | 2.4016 | 2.8061 | 16.1737 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.060924 | 0.060924 | 12.7642 | 435 | 453.7174 | 1.062 | 1.0678 | 298.15 | 0.32836 | 0.41407 | 0.65496 | 453 | 2816.5993 | 6.5855 | 0.56181 | 0.66086 | 21.47 | 117.4661 | 0.39768 | 0.076162 | 0.076162 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 75.583 | 50.5201 | 0.17463 | 0.23478 | 0.33553 | 75.583 | 63.1626 | 0.21675 | 0.24108 | 0.34453 | 4.3811 | 4.0092 | 0.49745 | 0.29097 | 0.56281 | 0.66456 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 54.746 | 0.19709 | 47.0218 | 0.16928 | 7.025 | 0.02529 | 0.088923 | 7.4383 | 0.026778 | 0.094155 | 0.063119 | 0.057761 | 227.2282 | 207.9403 | 0.004773 | 0.0027919 | 17.183 | 10.0508 | 0.010763 | 0.0094691 | 38.7477 | 34.0887 | 6.7827 | 6.8153 | 2.4016 | 2.7395 | 0.91262 | 0.89091 | 0.50089 | 0.59994 | 0.56181 | 0.66086 | 0.23478 | 0.33553 | 19.1655 | 2401.5617 | 2806.0506 | 0.65496 | 0.77044 | 75.583 | 108.0161 | 0.29011 | 0.33898 | 0.2124 | 0.24985 | 0.76455 | 0.48393 | 0.27369 | 0.31979 | 0.50172 | 0.6734 | 0.50771 | 0.4179 | 0.16928 | 0.094155 | 283.1589 | 252.0798
2013-06-27 | 122 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 19738.0112 | 19 | 56689.6331 | 17 | 2 | 5 | 345.398 | 70.006 | 180 | 2.8244 | 17 | 1250 | 61605.3186 | 9302.915 | 381.5503 | 11.1696 | 14.1029 | 37 | 27.1514 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 9.8486 | 180 | 2.9333 | 12.6472 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0605 | 423.0172 | 1017.636 |  | 594.6188 | 9606.2777 | 2362.068 | 822.4171 | 0.16249 | 22.4441 | 19.4461 | 0.02 | 0.05 | 30 | 165 | 453 | 618.398 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 465.2549 | 23.1013 | 1.1097 | 1.0105 | 121.6188 | 473 | 438 | 449.8987 | 168.4993 | 0.2189 | 0.027 | 1.06 | 8.615 | 8.615 | 618.398 | 594.6188 | 1.1097 | 1.1034 | 2.1846 | 1.9167 | 618.398 | 594.6188 | 12.7622 | 1.1097 | 1.1034 | 298.15 | 1.455 | 1.2765 | 618.398 | 6.4003 | 1.1097 | 298.15 | 0.72966 | 0.64017 | 2.3621 | 2.7424 | 19.4461 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.073251 | 0.073251 | 12.7622 | 435 | 449.8987 | 1.0622 | 1.0669 | 298.15 | 0.32839 | 0.39597 | 0.78455 | 453 | 2816.5993 | 6.5855 | 0.67296 | 0.64312 | 21.47 | 113.7162 | 0.38519 | 0.075632 | 0.075632 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 106.8341 | 46.8306 | 0.16233 | 0.32926 | 0.30799 | 106.8341 | 59.1068 | 0.20324 | 0.3379 | 0.31608 | 4.0683 | 3.9559 | 0.52685 | 0.31067 | 0.67578 | 0.64537 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 53.5124 | 0.19264 | 47.4982 | 0.17099 | 7.3469 | 0.026449 | 0.092998 | 7.2501 | 0.0261 | 0.091774 | 0.058612 | 0.056992 | 211.0028 | 205.1726 | 0.0050551 | 0.0029809 | 18.1984 | 10.7312 | 0.01218 | 0.0095682 | 43.8493 | 34.4455 | 6.4304 | 6.6983 | 2.3621 | 2.2024 | 1.059 | 0.88053 | 0.59971 | 0.56986 | 0.67296 | 0.64312 | 0.32926 | 0.30799 | 19.1625 | 2362.068 | 2742.4249 | 0.78455 | 0.74975 | 106.8341 | 99.934 | 0.29063 | 0.33743 | 0.25913 | 0.24764 | 0.78691 | 0.40097 | 0.27418 | 0.31833 | 0.53234 | 0.64718 | 0.47891 | 0.48927 | 0.17099 | 0.091774 | 273.0505 | 250.3492
2013-06-28 | 123 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 20540.4723 | 19 | 57610.7178 | 17 | 2 | 5 | 342.3465 | 68.0206 | 180 | 2.6965 | 17 | 1250 | 57127.6123 | 8749.8201 | 373.1755 | 11.401 | 14.1991 | 37 | 27.155 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 9.845 | 180 | 2.7981 | 12.6516 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0619 | 429.0122 | 1032.0579 |  | 603.0458 | 9745.7766 | 2400.4466 | 855.853 | 0.1691 | 21.9515 | 18.8946 | 0.02 | 0.05 | 30 | 165 | 453 | 615.3465 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 444.1929 | 22.0479 | 1.1089 | 1.0099 | 130.0458 | 473 | 438 | 450.9521 | 164.3944 | 0.2189 | 0.027 | 1.06 | 8.9652 | 8.9652 | 615.3465 | 603.0458 | 1.1089 | 1.1056 | 2.1503 | 2.0109 | 615.3465 | 603.0458 | 12.7666 | 1.1089 | 1.1056 | 298.15 | 1.4321 | 1.3392 | 615.3465 | 6.4025 | 1.1089 | 298.15 | 0.71819 | 0.67163 | 2.4004 | 2.8819 | 18.8946 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.071174 | 0.071174 | 12.7666 | 435 | 450.9521 | 1.0622 | 1.0671 | 298.15 | 0.32848 | 0.40105 | 0.74903 | 453 | 2816.5993 | 6.5855 | 0.6425 | 0.68741 | 21.47 | 113.7312 | 0.38524 | 0.075634 | 0.075634 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 104.4891 | 47.7989 | 0.16556 | 0.3227 | 0.36199 | 104.4891 | 59.5094 | 0.20458 | 0.33076 | 0.37103 | 4.4145 | 4.0724 | 0.53227 | 0.32194 | 0.64473 | 0.69063 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 54.9651 | 0.19787 | 46.4791 | 0.16732 | 7.5362 | 0.02713 | 0.095395 | 7.6324 | 0.027477 | 0.096613 | 0.0636 | 0.058672 | 228.9595 | 211.2179 | 0.0051071 | 0.0030891 | 18.3856 | 11.1206 | 0.01195 | 0.010089 | 43.0185 | 36.3189 | 6.815 | 6.9544 | 2.4004 | 2.6025 | 1.031 | 0.93818 | 0.57133 | 0.61624 | 0.6425 | 0.68741 | 0.3227 | 0.36199 | 19.1691 | 2400.4466 | 2881.9237 | 0.74903 | 0.80139 | 104.4891 | 117.2105 | 0.28382 | 0.34074 | 0.23776 | 0.25438 | 0.79814 | 0.37536 | 0.26775 | 0.32146 | 0.5177 | 0.65684 | 0.52659 | 0.50225 | 0.16732 | 0.096613 | 290.3636 | 258.6574
2013-07-02 | 125 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 20654.4537 | 19 | 58812.5397 | 17 | 2 | 5 | 350.3229 | 57.5646 | 180 | 2.3041 | 17 | 1250 | 56441.507 | 8498.3176 | 359.226 | 12.7943 | 15.533 | 37 | 27.6088 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 9.3912 | 180 | 2.7387 | 12.6522 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0621 | 429.8634 | 1034.1056 |  | 604.2423 | 9765.5909 | 2450.5225 | 860.6022 | 0.17004 | 21.1309 | 15.9902 | 0.02 | 0.05 | 30 | 165 | 453 | 623.3229 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 379.5538 | 18.8386 | 1.111 | 1.0106 | 131.2423 | 473 | 438 | 454.1614 | 169.1615 | 0.2189 | 0.027 | 1.06 | 9.015 | 9.015 | 623.3229 | 604.2423 | 1.111 | 1.1059 | 2.2426 | 2.0244 | 623.3229 | 604.2423 | 12.7672 | 1.111 | 1.1059 | 298.15 | 1.4935 | 1.3482 | 623.3229 | 6.4028 | 1.111 | 298.15 | 0.74902 | 0.67614 | 2.4505 | 2.9017 | 15.9902 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.060233 | 0.060233 | 12.7672 | 435 | 454.1614 | 1.0619 | 1.0679 | 298.15 | 0.32842 | 0.41629 | 0.64003 | 453 | 2816.5993 | 6.5855 | 0.549 | 0.69509 | 21.47 | 115.6302 | 0.39157 | 0.075902 | 0.075902 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 100.5833 | 53.6301 | 0.18499 | 0.3145 | 0.39245 | 100.5833 | 65.0917 | 0.22318 | 0.3221 | 0.40193 | 4.3219 | 4.0889 | 0.67635 | 0.29708 | 0.55104 | 0.69901 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 53.5917 | 0.19293 | 46.3417 | 0.16683 | 7.5503 | 0.027181 | 0.095573 | 7.736 | 0.02785 | 0.097924 | 0.062265 | 0.058908 | 224.1553 | 212.0698 | 0.0064897 | 0.0028505 | 23.3628 | 10.2618 | 0.012604 | 0.0098456 | 45.3733 | 35.4442 | 6.7724 | 6.9906 | 2.4505 | 2.4683 | 1.0773 | 0.93194 | 0.48877 | 0.63486 | 0.549 | 0.69509 | 0.3145 | 0.39245 | 19.17 | 2450.5225 | 2901.7381 | 0.64003 | 0.81035 | 100.5833 | 125.5131 | 0.28814 | 0.34119 | 0.20204 | 0.2558 | 0.78462 | 0.39019 | 0.27183 | 0.32188 | 0.4195 | 0.68122 | 0.5646 | 0.57286 | 0.16683 | 0.097924 | 292.8913 | 257.7758
2013-07-03 | 126 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 19855.8142 | 19 | 55926.6297 | 17 | 2 | 5 | 348.4528 | 68.6752 | 180 | 2.6787 | 17 | 1250 | 56637.448 | 8808.409 | 373.3314 | 12.079 | 14.6476 | 37 | 27.7272 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 9.2728 | 180 | 2.5686 | 12.6479 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0607 | 423.8975 | 1019.7538 |  | 595.8563 | 9626.7565 | 2330.2762 | 827.3256 | 0.16346 | 21.9607 | 19.0765 | 0.02 | 0.05 | 30 | 165 | 453 | 621.4528 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 441.2641 | 21.909 | 1.1105 | 1.0108 | 122.8563 | 473 | 438 | 451.091 | 170.3618 | 0.2189 | 0.027 | 1.06 | 8.6664 | 8.6664 | 621.4528 | 595.8563 | 1.1105 | 1.1037 | 2.2201 | 1.9304 | 621.4528 | 595.8563 | 12.7629 | 1.1105 | 1.1037 | 298.15 | 1.4786 | 1.2856 | 621.4528 | 6.4006 | 1.1105 | 298.15 | 0.7415 | 0.64475 | 2.3303 | 2.7629 | 19.0765 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.071859 | 0.071859 | 12.7629 | 435 | 451.091 | 1.0621 | 1.0671 | 298.15 | 0.32838 | 0.40158 | 0.74409 | 453 | 2816.5993 | 6.5855 | 0.63826 | 0.65017 | 21.47 | 116.1261 | 0.39322 | 0.075972 | 0.075972 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 104.5328 | 50.6366 | 0.17501 | 0.32479 | 0.37624 | 104.5328 | 61.3862 | 0.21083 | 0.33219 | 0.38481 | 4.1161 | 3.9731 | 0.58377 | 0.30575 | 0.64018 | 0.65325 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 54.3412 | 0.19563 | 47.3427 | 0.17043 | 7.3689 | 0.026528 | 0.093277 | 7.4736 | 0.026905 | 0.094602 | 0.0593 | 0.05724 | 213.4799 | 206.0653 | 0.0056013 | 0.0029337 | 20.1648 | 10.5613 | 0.012473 | 0.0095819 | 44.9044 | 34.4948 | 6.4463 | 6.736 | 2.3303 | 2.1816 | 1.077 | 0.88406 | 0.5664 | 0.57831 | 0.63826 | 0.65017 | 0.32479 | 0.37624 | 19.1635 | 2330.2762 | 2762.9036 | 0.74409 | 0.75797 | 104.5328 | 121.0919 | 0.28502 | 0.33794 | 0.24431 | 0.24887 | 0.81044 | 0.36339 | 0.26889 | 0.31881 | 0.49245 | 0.65415 | 0.57868 | 0.50886 | 0.17043 | 0.094602 | 278.5491 | 251.1213
2013-07-25 | 138 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 20418.6737 | 19 | 58947.2128 | 17 | 2 | 5 | 355.6394 | 79.4408 | 180 | 3.1217 | 17 | 1250 | 83067.5047 | 11147.3241 | 293.6057 | 9.5988 | 13.7199 | 37 | 29.0594 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 7.9406 | 180 | 4.1211 | 12.6509 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0617 | 428.1025 | 1029.8696 |  | 601.7671 | 9724.6032 | 2456.1339 | 850.7781 | 0.1681 | 17.2709 | 22.0669 | 0.02 | 0.05 | 30 | 165 | 453 | 628.6394 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 514.2373 | 25.5259 | 1.1124 | 1.0125 | 128.7671 | 473 | 438 | 447.4741 | 181.1653 | 0.2189 | 0.027 | 1.06 | 8.9121 | 8.9121 | 628.6394 | 601.7671 | 1.1124 | 1.1053 | 2.3046 | 1.9965 | 628.6394 | 601.7671 | 12.766 | 1.1124 | 1.1053 | 298.15 | 1.5348 | 1.3296 | 628.6394 | 6.4021 | 1.1124 | 298.15 | 0.76972 | 0.66682 | 2.4561 | 2.8608 | 22.0669 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.083123 | 0.083123 | 12.766 | 435 | 447.4741 | 1.0624 | 1.0663 | 298.15 | 0.32854 | 0.38479 | 0.86715 | 453 | 2816.5993 | 6.5855 | 0.74381 | 0.68278 | 21.47 | 121.7011 | 0.41179 | 0.076761 | 0.076761 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 82.2096 | 40.2564 | 0.14043 | 0.24981 | 0.26929 | 82.2096 | 57.5035 | 0.19789 | 0.25915 | 0.27937 | 4.1514 | 4.0549 | 0.5456 | 0.34519 | 0.74846 | 0.68815 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 52.502 | 0.18901 | 46.6279 | 0.16786 | 7.232 | 0.026035 | 0.091544 | 7.2837 | 0.026221 | 0.092199 | 0.059809 | 0.058418 | 215.3116 | 210.3058 | 0.005235 | 0.0033121 | 18.8461 | 11.9235 | 0.013112 | 0.010404 | 47.2029 | 37.4534 | 6.6075 | 6.9156 | 2.4561 | 2.2503 | 1.15 | 0.94485 | 0.66069 | 0.59966 | 0.74381 | 0.68278 | 0.24981 | 0.26929 | 19.1681 | 2456.1339 | 2860.7504 | 0.86715 | 0.79599 | 82.2096 | 88.6233 | 0.29213 | 0.34026 | 0.27688 | 0.25417 | 0.6993 | 1.0313 | 0.2756 | 0.321 | 0.54771 | 0.63466 | 0.39441 | 0.33584 | 0.16786 | 0.092199 | 281.3607 | 259.6827
2013-07-27 | 139 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 26161.2855 | 19 | 73477.5336 | 17 | 2 | 5 | 365.1457 | 77.7056 | 180 | 3.0683 | 17 | 1250 | 70902.4151 | 9836.5058 | 339.0266 | 11.9078 | 15.392 | 37 | 28.9751 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 8.0249 | 180 | 3.4842 | 12.6821 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0719 | 470.8884 | 1132.7979 |  | 661.9095 | 10722.8915 | 3061.5639 | 1090.0536 | 0.21537 | 19.9427 | 21.5849 | 0.02 | 0.05 | 30 | 165 | 453 | 638.1457 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 505.4297 | 25.027 | 1.1149 | 1.0139 | 188.9095 | 473 | 438 | 447.973 | 190.1727 | 0.2189 | 0.027 | 1.06 | 11.4185 | 11.4185 | 638.1457 | 661.9095 | 1.1149 | 1.1213 | 2.4233 | 2.7142 | 638.1457 | 661.9095 | 12.7974 | 1.1149 | 1.1213 | 298.15 | 1.6139 | 1.8077 | 638.1457 | 6.4179 | 1.1149 | 298.15 | 0.80938 | 0.90656 | 3.0616 | 3.859 | 21.5849 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.081308 | 0.081308 | 12.7974 | 435 | 447.973 | 1.0624 | 1.0664 | 298.15 | 0.32934 | 0.38806 | 0.85229 | 453 | 2816.5993 | 6.5855 | 0.73108 | 1.0064 | 21.47 | 121.3483 | 0.41062 | 0.076711 | 0.076711 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 94.9275 | 49.92 | 0.17263 | 0.2945 | 0.54969 | 94.9275 | 64.5017 | 0.22121 | 0.30362 | 0.56672 | 5.9337 | 4.8452 | 0.6348 | 0.49449 | 0.73544 | 1.0187 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 53.3557 | 0.19208 | 41.2435 | 0.14848 | 8.9345 | 0.032164 | 0.11309 | 9.5917 | 0.03453 | 0.12141 | 0.085486 | 0.069805 | 307.7506 | 251.2991 | 0.0060909 | 0.0047447 | 21.9273 | 17.0808 | 0.013951 | 0.014999 | 50.2225 | 53.9972 | 8.9952 | 8.7043 | 3.0616 | 4.4002 | 1.2258 | 1.4196 | 0.64977 | 0.92513 | 0.73108 | 1.0064 | 0.2945 | 0.54969 | 19.2154 | 3061.5639 | 3859.0387 | 0.85229 | 1.1733 | 94.9275 | 177.1883 | 0.28421 | 0.35824 | 0.21251 | 0.29256 | 0.72294 | 0.7331 | 0.26812 | 0.33796 | 0.50583 | 0.65168 | 0.54618 | 0.40282 | 0.14848 | 0.12141 | 379.9004 | 322.377
2013-07-28 | 140 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 27743.3612 | 19 | 80165.5589 | 17 | 2 | 5 | 378.9336 | 90.5966 | 180 | 3.543 | 17 | 1250 | 66156.3933 | 8666.0849 | 296.9072 | 10.4908 | 13.9111 | 37 | 27.9045 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 9.0955 | 180 | 3.4202 | 12.6907 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0748 | 482.6388 | 1161.0655 |  | 678.4266 | 10997.9175 | 3340.2316 | 1155.9734 | 0.2284 | 17.4651 | 25.1657 | 0.02 | 0.05 | 30 | 165 | 453 | 651.9336 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 583.6271 | 28.8795 | 1.1186 | 1.0168 | 205.4266 | 473 | 438 | 444.1205 | 207.8131 | 0.2189 | 0.027 | 1.06 | 12.109 | 12.109 | 651.9336 | 678.4266 | 1.1186 | 1.1257 | 2.5924 | 2.9253 | 651.9336 | 678.4266 | 12.8061 | 1.1186 | 1.1257 | 298.15 | 1.7266 | 1.9482 | 651.9336 | 6.4223 | 1.1186 | 298.15 | 0.86587 | 0.97705 | 3.3402 | 4.1341 | 25.1657 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.094796 | 0.094796 | 12.8061 | 435 | 444.1205 | 1.0627 | 1.0655 | 298.15 | 0.32965 | 0.37056 | 0.98416 | 453 | 2816.5993 | 6.5855 | 0.84418 | 1.0988 | 21.47 | 116.8678 | 0.39569 | 0.076077 | 0.076077 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 83.134 | 43.9898 | 0.15287 | 0.25466 | 0.59723 | 83.134 | 58.3038 | 0.20056 | 0.2625 | 0.61562 | 6.1764 | 5.0497 | 0.64751 | 0.57368 | 0.84664 | 1.1118 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 51.1532 | 0.18415 | 40.1706 | 0.14461 | 9.1416 | 0.03291 | 0.11572 | 10.1154 | 0.036416 | 0.12804 | 0.088983 | 0.072751 | 320.3393 | 261.903 | 0.0062129 | 0.0055045 | 22.3665 | 19.8161 | 0.015143 | 0.016763 | 54.5139 | 60.3479 | 9.5166 | 9.1838 | 3.3402 | 4.7378 | 1.356 | 1.5777 | 0.74939 | 1.004 | 0.84418 | 1.0988 | 0.25466 | 0.59723 | 19.2284 | 3340.2316 | 4134.0647 | 0.98416 | 1.281 | 83.134 | 194.967 | 0.2924 | 0.36189 | 0.23142 | 0.30122 | 0.68262 | 0.5722 | 0.27585 | 0.3414 | 0.53646 | 0.63638 | 0.54353 | 0.30166 | 0.14461 | 0.12804 | 397.2197 | 342.067
2013-07-29 | 141 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 27297.6078 | 19 | 78434.33 | 17 | 2 | 5 | 379.6169 | 139.7057 | 180 | 5.5764 | 17 | 1250 | 79906.4312 | 11232.7659 | 273.2608 | 9.7745 | 14.362 | 37 | 28.4493 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 8.5507 | 180 | 4.5875 | 12.6883 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.074 | 479.3297 | 1153.1049 |  | 673.7752 | 10920.4283 | 3268.0971 | 1137.4003 | 0.22473 | 16.0742 | 38.8071 | 0.02 | 0.05 | 30 | 165 | 453 | 652.6169 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 918.5935 | 45.4632 | 1.1188 | 1.0197 | 200.7752 | 473 | 438 | 427.5368 | 225.0801 | 0.2189 | 0.027 | 1.06 | 11.9145 | 11.9145 | 652.6169 | 673.7752 | 1.1188 | 1.1245 | 2.6003 | 2.8653 | 652.6169 | 673.7752 | 12.8037 | 1.1188 | 1.1245 | 298.15 | 1.7318 | 1.9083 | 652.6169 | 6.4211 | 1.1188 | 298.15 | 0.86851 | 0.957 | 3.2681 | 4.0566 | 38.8071 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.14618 | 0.14618 | 12.8037 | 435 | 427.5368 | 1.0638 | 1.0615 | 298.15 | 0.32995 | 0.29794 | 1.549 | 453 | 2816.5993 | 6.5855 | 1.3287 | 1.0739 | 21.47 | 119.1481 | 0.40329 | 0.0764 | 0.0764 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 76.513 | 40.9916 | 0.14288 | 0.23287 | 0.43719 | 76.513 | 60.1908 | 0.20685 | 0.24255 | 0.45536 | 6.0461 | 4.9926 | 0.21936 | 0.68262 | 1.3333 | 1.087 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 51.3897 | 0.185 | 40.4602 | 0.14566 | 8.8774 | 0.031959 | 0.11237 | 9.7346 | 0.035044 | 0.12322 | 0.087105 | 0.071929 | 313.5798 | 258.9442 | 0.0021047 | 0.0065498 | 7.5771 | 23.5793 | 0.015166 | 0.018104 | 54.5988 | 65.1753 | 9.3142 | 9.0492 | 3.2681 | 4.5386 | 1.4339 | 1.6103 | 1.1825 | 0.92771 | 1.3287 | 1.0739 | 0.23287 | 0.43719 | 19.2247 | 3268.0971 | 4056.5755 | 1.549 | 1.2519 | 76.513 | 143.648 | 0.29075 | 0.3609 | 0.37017 | 0.29919 | 0.73254 | 1.1025 | 0.2743 | 0.34047 | 0.84353 | 0.5761 | 0.40711 | 0.17526 | 0.14566 | 0.12322 | 375.7557 | 347.6988
2013-07-30 | 142 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 20488.6527 | 19 | 58922.2111 | 17 | 2 | 5 | 367.7698 | 121.092 | 180 | 4.7815 | 17 | 1250 | 61585.4487 | 8152.2356 | 273.4712 | 10.8395 | 13.8229 | 37 | 27.1424 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 9.8576 | 180 | 2.9835 | 12.6513 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0618 | 428.6252 | 1031.1269 |  | 602.5018 | 9736.7683 | 2455.0921 | 853.6939 | 0.16867 | 16.0865 | 33.6367 | 0.02 | 0.05 | 30 | 165 | 453 | 640.7698 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 787.6434 | 39.0962 | 1.1156 | 1.0166 | 129.5018 | 473 | 438 | 433.9038 | 206.866 | 0.2189 | 0.027 | 1.06 | 8.9426 | 8.9426 | 640.7698 | 602.5018 | 1.1156 | 1.1055 | 2.4489 | 2.0047 | 640.7698 | 602.5018 | 12.7663 | 1.1156 | 1.1055 | 298.15 | 1.6309 | 1.3351 | 640.7698 | 6.4023 | 1.1156 | 298.15 | 0.81792 | 0.66958 | 2.4551 | 2.8729 | 33.6367 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.12671 | 0.12671 | 12.7663 | 435 | 433.9038 | 1.0634 | 1.063 | 298.15 | 0.32885 | 0.32408 | 1.3282 | 453 | 2816.5993 | 6.5855 | 1.1393 | 0.68869 | 21.47 | 113.6783 | 0.38506 | 0.075626 | 0.075626 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 76.5719 | 45.4489 | 0.15773 | 0.23529 | 0.33855 | 76.5719 | 57.935 | 0.19933 | 0.24159 | 0.34762 | 4.0386 | 4.065 | 0.28952 | 0.44907 | 1.1397 | 0.69192 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 51.8567 | 0.18668 | 46.5422 | 0.16755 | 7.1923 | 0.025892 | 0.091041 | 7.5545 | 0.027196 | 0.095626 | 0.058185 | 0.058564 | 209.465 | 210.8301 | 0.0027779 | 0.0043089 | 10.0005 | 15.512 | 0.014063 | 0.011944 | 50.6258 | 42.999 | 6.4937 | 6.9379 | 2.4551 | 2.0036 | 1.3069 | 1.0111 | 1.0126 | 0.56199 | 1.1393 | 0.68869 | 0.23529 | 0.33855 | 19.1687 | 2455.0921 | 2872.9154 | 1.3282 | 0.80288 | 76.5719 | 110.1752 | 0.29101 | 0.34054 | 0.42265 | 0.25549 | 0.6898 | 0.41024 | 0.27454 | 0.32126 | 0.77765 | 0.55584 | 0.49159 | 0.20653 | 0.16755 | 0.095626 | 270.0913 | 269.3411
2013-07-31 | 143 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 27768.3649 | 19 | 81055.0361 | 17 | 2 | 5 | 388.1697 | 134.1783 | 180 | 5.3311 | 17 | 1250 | 62074.3706 | 8763.1892 | 245.6976 | 10.1763 | 14.2969 | 37 | 27.7521 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 9.2479 | 180 | 4.1205 | 12.6909 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0749 | 482.8244 | 1161.5119 |  | 678.6875 | 11002.2641 | 3377.2932 | 1157.0152 | 0.22861 | 14.4528 | 37.2717 | 0.02 | 0.05 | 30 | 165 | 453 | 661.1697 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 878.1773 | 43.4542 | 1.1211 | 1.0209 | 205.6875 | 473 | 438 | 429.5458 | 231.6239 | 0.2189 | 0.027 | 1.06 | 12.1199 | 12.1199 | 661.1697 | 678.6875 | 1.1211 | 1.1258 | 2.7069 | 2.9287 | 661.1697 | 678.6875 | 12.8063 | 1.1211 | 1.1258 | 298.15 | 1.8028 | 1.9505 | 661.1697 | 6.4224 | 1.1211 | 298.15 | 0.90409 | 0.97817 | 3.3773 | 4.1384 | 37.2717 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.1404 | 0.1404 | 12.8063 | 435 | 429.5458 | 1.0637 | 1.062 | 298.15 | 0.32997 | 0.30644 | 1.4808 | 453 | 2816.5993 | 6.5855 | 1.2702 | 1.1026 | 21.47 | 116.2302 | 0.39357 | 0.075987 | 0.075987 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 68.7953 | 42.6736 | 0.14848 | 0.21014 | 0.49413 | 68.7953 | 59.9185 | 0.20594 | 0.21796 | 0.51251 | 6.0358 | 5.0529 | 0.34296 | 0.68181 | 1.2726 | 1.1155 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 50.1502 | 0.18054 | 40.1547 | 0.14456 | 8.8146 | 0.031733 | 0.11158 | 9.9789 | 0.035924 | 0.12632 | 0.086958 | 0.072797 | 313.0474 | 262.0683 | 0.0032908 | 0.006542 | 11.8467 | 23.5511 | 0.015917 | 0.018288 | 57.301 | 65.8366 | 9.4131 | 9.1913 | 3.3773 | 4.5376 | 1.4963 | 1.644 | 1.1298 | 0.96224 | 1.2702 | 1.1026 | 0.21014 | 0.49413 | 19.2286 | 3377.2932 | 4138.4113 | 1.4808 | 1.2855 | 68.7953 | 161.7686 | 0.29538 | 0.36194 | 0.3479 | 0.302 | 0.73566 | 0.76235 | 0.27866 | 0.34145 | 0.76713 | 0.58529 | 0.44814 | 0.16543 | 0.14456 | 0.12632 | 382.1951 | 351.456
2013-08-01 | 144 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 27615.9064 | 19 | 80321.9361 | 17 | 2 | 5 | 391.7955 | 136.4917 | 180 | 5.391 | 17 | 1250 | 65287.2068 | 9100.6697 | 277.826 | 9.8954 | 13.9673 | 37 | 27.5963 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 9.4037 | 180 | 4.0719 | 12.6901 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0746 | 481.6928 | 1158.7896 |  | 677.0968 | 10975.761 | 3346.7473 | 1150.6628 | 0.22735 | 16.3427 | 37.9144 | 0.02 | 0.05 | 30 | 165 | 453 | 664.7955 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 888.0519 | 43.9457 | 1.1221 | 1.0216 | 204.0968 | 473 | 438 | 429.0543 | 235.7412 | 0.2189 | 0.027 | 1.06 | 12.0534 | 12.0534 | 664.7955 | 677.0968 | 1.1221 | 1.1254 | 2.7521 | 2.9081 | 664.7955 | 677.0968 | 12.8054 | 1.1221 | 1.1254 | 298.15 | 1.8329 | 1.9368 | 664.7955 | 6.4219 | 1.1221 | 298.15 | 0.9192 | 0.9713 | 3.3467 | 4.1119 | 37.9144 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.14282 | 0.14282 | 12.8054 | 435 | 429.0543 | 1.0637 | 1.0619 | 298.15 | 0.32996 | 0.30435 | 1.4975 | 453 | 2816.5993 | 6.5855 | 1.2845 | 1.095 | 21.47 | 115.5779 | 0.39139 | 0.075895 | 0.075895 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 77.7913 | 41.4979 | 0.14456 | 0.23702 | 0.49177 | 77.7913 | 58.5393 | 0.20134 | 0.24575 | 0.50989 | 5.9546 | 5.0334 | 0.36123 | 0.68026 | 1.2877 | 1.1075 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 50.1268 | 0.18046 | 40.2525 | 0.14491 | 9.0103 | 0.032437 | 0.11405 | 9.9305 | 0.03575 | 0.1257 | 0.085788 | 0.072516 | 308.8352 | 261.0593 | 0.003466 | 0.0065272 | 12.4776 | 23.4977 | 0.016265 | 0.018219 | 58.5525 | 65.5891 | 9.3013 | 9.1453 | 3.3467 | 4.3922 | 1.5285 | 1.6324 | 1.1417 | 0.95217 | 1.2845 | 1.095 | 0.23702 | 0.49177 | 19.2274 | 3346.7473 | 4111.9081 | 1.4975 | 1.2765 | 77.7913 | 161.4045 | 0.29432 | 0.36161 | 0.35375 | 0.30155 | 0.72639 | 0.7238 | 0.27766 | 0.34114 | 0.75965 | 0.58328 | 0.44911 | 0.18452 | 0.14491 | 0.1257 | 379.8653 | 350.1462
2013-08-02 | 145 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 27025.292 | 19 | 77994.8361 | 17 | 2 | 5 | 384.1835 | 126.8993 | 180 | 5.0284 | 17 | 1250 | 63675.9767 | 7200.6273 | 276.975 | 9.3102 | 13.067 | 37 | 27.0547 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 9.9453 | 180 | 3.7567 | 12.6868 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0735 | 477.3075 | 1148.2402 |  | 670.9327 | 10873.0893 | 3249.7848 | 1126.0538 | 0.22249 | 16.2926 | 35.2498 | 0.02 | 0.05 | 30 | 165 | 453 | 657.1835 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 828.3168 | 41 | 1.12 | 1.0197 | 197.9327 | 473 | 438 | 432 | 225.1835 | 0.2189 | 0.027 | 1.06 | 11.7956 | 11.7956 | 657.1835 | 670.9327 | 1.12 | 1.1237 | 2.6564 | 2.8288 | 657.1835 | 670.9327 | 12.8022 | 1.12 | 1.1237 | 298.15 | 1.7692 | 1.884 | 657.1835 | 6.4203 | 1.12 | 298.15 | 0.88725 | 0.94482 | 3.2498 | 4.0092 | 35.2498 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.13278 | 0.13278 | 12.8022 | 435 | 432 | 1.0635 | 1.0626 | 298.15 | 0.32982 | 0.31679 | 1.3968 | 453 | 2816.5993 | 6.5855 | 1.1981 | 1.0597 | 21.47 | 113.3115 | 0.38384 | 0.075574 | 0.075574 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 77.553 | 39.0488 | 0.1364 | 0.23504 | 0.4985 | 77.553 | 54.7711 | 0.18879 | 0.24307 | 0.51554 | 5.8894 | 4.9576 | 0.37403 | 0.64026 | 1.2003 | 1.0709 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 50.9037 | 0.18325 | 40.6418 | 0.14631 | 8.8353 | 0.031807 | 0.11184 | 9.7697 | 0.035171 | 0.12367 | 0.084849 | 0.071424 | 305.4556 | 257.1255 | 0.0035888 | 0.0061433 | 12.9198 | 22.116 | 0.01556 | 0.017372 | 56.0157 | 62.5404 | 9.1392 | 8.9668 | 3.2498 | 4.3224 | 1.4524 | 1.5672 | 1.0653 | 0.92694 | 1.1981 | 1.0597 | 0.23504 | 0.4985 | 19.2225 | 3249.7848 | 4009.2364 | 1.3968 | 1.2354 | 77.553 | 164.485 | 0.29204 | 0.36029 | 0.33715 | 0.29821 | 0.58928 | 0.5735 | 0.27551 | 0.33989 | 0.74014 | 0.59146 | 0.47041 | 0.19617 | 0.14631 | 0.12367 | 374.3912 | 341.782
2013-08-03 | 146 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 24024.6785 | 19 | 66561.5983 | 17 | 2 | 5 | 374.5319 | 57.0355 | 180 | 2.2394 | 17 | 1250 | 48434.3096 | 7846.7685 | 228.8354 | 10.2312 | 13.9856 | 37 | 27.1575 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 9.8425 | 180 | 3.7544 | 12.6705 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0681 | 454.994 | 1094.5614 |  | 639.5674 | 10351.4665 | 2773.3999 | 1001.0283 | 0.19778 | 13.4609 | 15.8432 | 0.02 | 0.05 | 30 | 165 | 453 | 647.5319 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 368.8893 | 18.2828 | 1.1174 | 1.0143 | 166.5674 | 473 | 438 | 454.7172 | 192.8146 | 0.2189 | 0.027 | 1.06 | 10.486 | 10.486 | 647.5319 | 639.5674 | 1.1174 | 1.1153 | 2.5345 | 2.4381 | 647.5319 | 639.5674 | 12.7857 | 1.1174 | 1.1153 | 298.15 | 1.688 | 1.6238 | 647.5319 | 6.4121 | 1.1174 | 298.15 | 0.84651 | 0.81433 | 2.7734 | 3.4876 | 15.8432 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.059679 | 0.059679 | 12.7857 | 435 | 454.7172 | 1.0619 | 1.068 | 298.15 | 0.32889 | 0.41955 | 0.62205 | 453 | 2816.5993 | 6.5855 | 0.53358 | 0.88859 | 21.47 | 113.7415 | 0.38527 | 0.075635 | 0.075635 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 64.0739 | 42.9031 | 0.14925 | 0.19582 | 0.3955 | 64.0739 | 58.6155 | 0.2016 | 0.20245 | 0.4089 | 5.1781 | 4.5602 | 0.88518 | 0.37533 | 0.53438 | 0.89616 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 53.4776 | 0.19252 | 42.9241 | 0.15453 | 7.763 | 0.027947 | 0.098266 | 8.7022 | 0.031328 | 0.11015 | 0.074601 | 0.065699 | 268.5623 | 236.5166 | 0.0084933 | 0.0036013 | 30.5759 | 12.9647 | 0.014705 | 0.012492 | 52.9373 | 44.972 | 7.9515 | 8.0478 | 2.7734 | 3.3064 | 1.2684 | 1.2042 | 0.4739 | 0.82891 | 0.53358 | 0.88859 | 0.19582 | 0.3955 | 19.1978 | 2773.3999 | 3487.6136 | 0.62205 | 1.0359 | 64.0739 | 129.4135 | 0.28036 | 0.35255 | 0.16887 | 0.28122 | 0.84423 | 0.58294 | 0.26449 | 0.3326 | 0.34869 | 0.68833 | 0.44508 | 0.36699 | 0.15453 | 0.11015 | 352.0755 | 294.4532
2013-08-04 | 147 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 27478.3429 | 19 | 78788.6942 | 17 | 2 | 5 | 372.4197 | 66.3007 | 180 | 2.6104 | 17 | 1250 | 58353.4845 | 9115.9314 | 317.8958 | 10.6982 | 13.2854 | 37 | 27.4074 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 9.5926 | 180 | 2.5872 | 12.6893 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0743 | 480.6716 | 1156.3329 |  | 675.6614 | 10951.8471 | 3282.8623 | 1144.931 | 0.22622 | 18.6998 | 18.4169 | 0.02 | 0.05 | 30 | 165 | 453 | 645.4197 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 430.011 | 21.2806 | 1.1169 | 1.0145 | 202.6614 | 473 | 438 | 451.7194 | 193.7002 | 0.2189 | 0.027 | 1.06 | 11.9934 | 11.9934 | 645.4197 | 675.6614 | 1.1169 | 1.125 | 2.5125 | 2.8895 | 645.4197 | 675.6614 | 12.8047 | 1.1169 | 1.125 | 298.15 | 1.6733 | 1.9244 | 645.4197 | 6.4216 | 1.1169 | 298.15 | 0.83918 | 0.96511 | 3.2829 | 4.088 | 18.4169 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.069374 | 0.069374 | 12.8047 | 435 | 451.7194 | 1.0621 | 1.0673 | 298.15 | 0.32944 | 0.40587 | 0.72512 | 453 | 2816.5993 | 6.5855 | 0.62199 | 1.0822 | 21.47 | 114.7874 | 0.38876 | 0.075783 | 0.075783 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 89.0108 | 44.8576 | 0.15576 | 0.27317 | 0.76288 | 89.0108 | 55.6855 | 0.19184 | 0.27952 | 0.78061 | 6.198 | 5.0158 | 0.79127 | 0.50575 | 0.62266 | 1.0943 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 51.8902 | 0.1868 | 40.3416 | 0.14523 | 9.176 | 0.033033 | 0.11615 | 10.1859 | 0.036669 | 0.12893 | 0.089295 | 0.072263 | 321.4602 | 260.1466 | 0.0075923 | 0.0048527 | 27.3324 | 17.4696 | 0.014529 | 0.015742 | 52.3048 | 56.672 | 9.4809 | 9.1038 | 3.2829 | 4.777 | 1.2675 | 1.5186 | 0.55261 | 1.0128 | 0.62199 | 1.0822 | 0.27317 | 0.76288 | 19.2262 | 3282.8623 | 4087.9942 | 0.72512 | 1.2616 | 89.0108 | 248.5778 | 0.29015 | 0.36131 | 0.17215 | 0.29952 | 0.81407 | 0.34964 | 0.27372 | 0.34085 | 0.4112 | 0.66696 | 0.70493 | 0.43919 | 0.14523 | 0.12893 | 401.0974 | 334.2881
2013-08-05 | 148 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 24895.0725 | 19 | 69426.4847 | 17 | 2 | 5 | 354.4596 | 71.5933 | 180 | 2.8128 | 17 | 1250 | 64894.2779 | 7778.8878 | 249.0897 | 10.0231 | 13.7186 | 37 | 27.86 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 9.14 | 180 | 3.6955 | 12.6753 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0696 | 461.4724 | 1110.1463 |  | 648.6739 | 10502.7747 | 2892.7702 | 1037.2947 | 0.20495 | 14.6523 | 19.887 | 0.02 | 0.05 | 30 | 165 | 453 | 627.4596 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 463.343 | 22.9555 | 1.1121 | 1.0119 | 175.6739 | 473 | 438 | 450.0445 | 177.4151 | 0.2189 | 0.027 | 1.06 | 10.8659 | 10.8659 | 627.4596 | 648.6739 | 1.1121 | 1.1177 | 2.2951 | 2.5494 | 627.4596 | 648.6739 | 12.7905 | 1.1121 | 1.1177 | 298.15 | 1.5285 | 1.6979 | 627.4596 | 6.4145 | 1.1121 | 298.15 | 0.76656 | 0.85148 | 2.8928 | 3.6389 | 19.887 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.074912 | 0.074912 | 12.7905 | 435 | 450.0445 | 1.0622 | 1.0669 | 298.15 | 0.32912 | 0.39753 | 0.78132 | 453 | 2816.5993 | 6.5855 | 0.6702 | 0.93303 | 21.47 | 116.6816 | 0.39507 | 0.076051 | 0.076051 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 69.7451 | 42.0323 | 0.14634 | 0.21275 | 0.44228 | 69.7451 | 57.4982 | 0.19788 | 0.21985 | 0.45705 | 5.678 | 4.6776 | 0.60413 | 0.44222 | 0.6719 | 0.9424 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 54.355 | 0.19568 | 42.203 | 0.15193 | 8.081 | 0.029092 | 0.10229 | 9.0523 | 0.032588 | 0.11459 | 0.081803 | 0.06739 | 294.4898 | 242.6038 | 0.0057967 | 0.0042431 | 20.868 | 15.2752 | 0.01299 | 0.013702 | 46.7623 | 49.3279 | 8.5708 | 8.3165 | 2.8928 | 4.1217 | 1.131 | 1.3003 | 0.59529 | 0.85812 | 0.6702 | 0.93303 | 0.21275 | 0.44228 | 19.205 | 2892.7702 | 3638.9218 | 0.78132 | 1.0877 | 69.7451 | 144.9931 | 0.2822 | 0.35499 | 0.20471 | 0.28499 | 0.62465 | 0.64428 | 0.26623 | 0.3349 | 0.49631 | 0.65992 | 0.47402 | 0.31744 | 0.15193 | 0.11459 | 362.1202 | 307.2069
2013-08-13 | 151 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 27258.4886 | 19 | 80970.7631 | 17 | 2 | 5 | 377.0504 | 88.2484 | 180 | 3.4848 | 17 | 1250 | 59916.2257 | 6740.6121 | 267.5644 | 9.7862 | 13.1463 | 37 | 27.9043 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 9.0957 | 180 | 3.3601 | 12.6881 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0739 | 479.0392 | 1152.4061 |  | 673.3669 | 10913.6279 | 3373.7818 | 1135.7704 | 0.22441 | 15.7391 | 24.5134 | 0.02 | 0.05 | 30 | 165 | 453 | 650.0504 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 574.0441 | 28.4112 | 1.1181 | 1.0164 | 200.3669 | 473 | 438 | 444.5888 | 205.4616 | 0.2189 | 0.027 | 1.06 | 11.8974 | 11.8974 | 650.0504 | 673.3669 | 1.1181 | 1.1244 | 2.5688 | 2.86 | 650.0504 | 673.3669 | 12.8035 | 1.1181 | 1.1244 | 298.15 | 1.7108 | 1.9048 | 650.0504 | 6.421 | 1.1181 | 298.15 | 0.85797 | 0.95525 | 3.3738 | 4.0498 | 24.5134 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.092339 | 0.092339 | 12.8035 | 435 | 444.5888 | 1.0626 | 1.0656 | 298.15 | 0.32958 | 0.37262 | 0.968 | 453 | 2816.5993 | 6.5855 | 0.83032 | 1.071 | 21.47 | 116.8671 | 0.39569 | 0.076077 | 0.076077 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 74.918 | 41.0407 | 0.14304 | 0.22804 | 0.58432 | 74.918 | 55.1032 | 0.1899 | 0.23498 | 0.6021 | 5.9548 | 4.9876 | 0.64325 | 0.55346 | 0.83188 | 1.0834 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 49.8418 | 0.17943 | 40.486 | 0.14575 | 8.825 | 0.03177 | 0.11171 | 9.9573 | 0.035846 | 0.12604 | 0.085791 | 0.071857 | 308.8493 | 258.6834 | 0.006172 | 0.0053105 | 22.2192 | 19.1177 | 0.014939 | 0.016274 | 53.7811 | 58.5879 | 9.3286 | 9.0374 | 3.3738 | 4.581 | 1.3382 | 1.5321 | 0.73798 | 0.97869 | 0.83032 | 1.071 | 0.22804 | 0.58432 | 19.2244 | 3373.7818 | 4049.775 | 0.968 | 1.2486 | 74.918 | 191.9682 | 0.30059 | 0.36081 | 0.23166 | 0.29882 | 0.58625 | 0.55624 | 0.28357 | 0.34039 | 0.53429 | 0.63877 | 0.54556 | 0.27464 | 0.14575 | 0.12604 | 384.8497 | 336.389
2013-08-14 | 152 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 25256.6746 | 19 | 72845.6389 | 17 | 2 | 5 | 353.2532 | 71.7956 | 180 | 2.7854 | 17 | 1250 | 48075.597 | 6544.587 | 191.2004 | 9.3234 | 12.9772 | 37 | 27.3878 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 9.6122 | 180 | 3.6539 | 12.6772 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0703 | 464.1625 | 1116.6176 |  | 652.4552 | 10565.6351 | 3035.235 | 1052.3614 | 0.20793 | 11.2471 | 19.9432 | 0.02 | 0.05 | 30 | 165 | 453 | 626.2532 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 458.8425 | 22.729 | 1.1118 | 1.0117 | 179.4552 | 473 | 438 | 450.271 | 175.9822 | 0.2189 | 0.027 | 1.06 | 11.0237 | 11.0237 | 626.2532 | 652.4552 | 1.1118 | 1.1187 | 2.2813 | 2.5961 | 626.2532 | 652.4552 | 12.7925 | 1.1118 | 1.1187 | 298.15 | 1.5193 | 1.729 | 626.2532 | 6.4154 | 1.1118 | 298.15 | 0.76195 | 0.86709 | 3.0352 | 3.7018 | 19.9432 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.075124 | 0.075124 | 12.7925 | 435 | 450.271 | 1.0622 | 1.0669 | 298.15 | 0.32916 | 0.39865 | 0.77373 | 453 | 2816.5993 | 6.5855 | 0.66369 | 0.95299 | 21.47 | 114.7056 | 0.38849 | 0.075771 | 0.075771 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 53.5361 | 39.1038 | 0.13659 | 0.16227 | 0.44906 | 53.5361 | 54.3957 | 0.18754 | 0.16766 | 0.46399 | 5.7072 | 4.7258 | 0.60161 | 0.45246 | 0.66339 | 0.96222 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 52.6185 | 0.18943 | 41.9188 | 0.15091 | 7.5865 | 0.027312 | 0.096032 | 9.1696 | 0.033011 | 0.11607 | 0.082223 | 0.068085 | 296.0031 | 245.1061 | 0.0057724 | 0.0043414 | 20.7808 | 15.6291 | 0.012872 | 0.013991 | 46.3378 | 50.3684 | 8.7424 | 8.4276 | 3.0352 | 4.2982 | 1.1207 | 1.3303 | 0.58857 | 0.87786 | 0.66369 | 0.95299 | 0.16227 | 0.44906 | 19.2079 | 3035.235 | 3701.7823 | 0.77373 | 1.111 | 53.5361 | 148.1544 | 0.29186 | 0.35595 | 0.19982 | 0.28692 | 0.70939 | 0.58049 | 0.27534 | 0.3358 | 0.49452 | 0.65989 | 0.47122 | 0.2445 | 0.15091 | 0.11607 | 363.1218 | 311.1037
2013-08-16 | 154 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 26559.852 | 19 | 77261.385 | 17 | 2 | 5 | 369.7377 | 84.4772 | 180 | 3.3888 | 17 | 1250 | 43471.3856 | 0 | 169.6388 | 10.5364 | 14.2685 | 37 | 27.608 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 9.392 | 180 | 3.7321 | 12.6843 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0727 | 473.8501 | 1139.9228 |  | 666.0727 | 10792.1778 | 3219.2244 | 1106.6605 | 0.21866 | 9.9788 | 23.4659 | 0.02 | 0.05 | 30 | 165 | 453 | 642.7377 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 558.2277 | 27.6367 | 1.1161 | 1.0151 | 193.0727 | 473 | 438 | 445.3633 | 197.3744 | 0.2189 | 0.027 | 1.06 | 11.5925 | 11.5925 | 642.7377 | 666.0727 | 1.1161 | 1.1224 | 2.479 | 2.7669 | 642.7377 | 666.0727 | 12.7996 | 1.1161 | 1.1224 | 298.15 | 1.651 | 1.8427 | 642.7377 | 6.419 | 1.1161 | 298.15 | 0.82799 | 0.92414 | 3.2192 | 3.9283 | 23.4659 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.088393 | 0.088393 | 12.7996 | 435 | 445.3633 | 1.0626 | 1.0658 | 298.15 | 0.32946 | 0.37606 | 0.94133 | 453 | 2816.5993 | 6.5855 | 0.80744 | 1.0299 | 21.47 | 115.627 | 0.39156 | 0.075902 | 0.075902 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 47.4989 | 44.1803 | 0.1535 | 0.14556 | 0.49795 | 47.4989 | 59.7996 | 0.20554 | 0.15045 | 0.51467 | 5.8942 | 4.8973 | 0.60251 | 0.52515 | 0.80677 | 1.0411 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 51.2718 | 0.18458 | 40.961 | 0.14746 | 7.6234 | 0.027444 | 0.096499 | 9.6332 | 0.034679 | 0.12194 | 0.084918 | 0.070555 | 305.7059 | 253.9975 | 0.0057811 | 0.0050388 | 20.812 | 18.1398 | 0.014227 | 0.015561 | 51.2187 | 56.0194 | 9.1135 | 8.8256 | 3.2192 | 4.4598 | 1.275 | 1.4667 | 0.71905 | 0.94153 | 0.80744 | 1.0299 | 0.14556 | 0.49795 | 19.2187 | 3219.2244 | 3928.3249 | 0.94133 | 1.2007 | 47.4989 | 162.4889 | 0.29436 | 0.3592 | 0.23119 | 0.2949 | 0 | 0.62499 | 0.2777 | 0.33887 | 0.54409 | 0.64195 | 0.48348 | 0.18027 | 0.14746 | 0.12194 | 377.7367 | 328.1568
2013-08-25 | 155 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 24898.6144 | 19 | 67323.1106 | 17 | 2 | 5 | 377.4563 | 76.2741 | 180 | 3.0058 | 17 | 1250 | 9212.416 | 1003.7216 | 45.3735 | 15.244 | 17.7042 | 37 | 28.6374 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 8.3626 | 180 | 2.4603 | 12.6753 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0697 | 461.4988 | 1110.2097 |  | 648.7109 | 10503.3904 | 2805.1296 | 1037.4423 | 0.20498 | 2.669 | 21.1873 | 0.02 | 0.05 | 30 | 165 | 453 | 650.4563 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 495.1486 | 24.5312 | 1.1182 | 1.0158 | 175.7109 | 473 | 438 | 448.4688 | 201.9875 | 0.2189 | 0.027 | 1.06 | 10.8674 | 10.8674 | 650.4563 | 648.7109 | 1.1182 | 1.1177 | 2.5711 | 2.5498 | 650.4563 | 648.7109 | 12.7905 | 1.1182 | 1.1177 | 298.15 | 1.7124 | 1.6982 | 650.4563 | 6.4145 | 1.1182 | 298.15 | 0.85876 | 0.85164 | 2.8051 | 3.6395 | 21.1873 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.07981 | 0.07981 | 12.7905 | 435 | 448.4688 | 1.0623 | 1.0665 | 298.15 | 0.32915 | 0.39016 | 0.83496 | 453 | 2816.5993 | 6.5855 | 0.7162 | 0.93838 | 21.47 | 119.9353 | 0.40591 | 0.076511 | 0.076511 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 12.7046 | 63.8821 | 0.21915 | 0.040582 | 0.7228 | 12.7046 | 74.1786 | 0.25345 | 0.041444 | 0.73815 | 5.4911 | 4.6781 | 0.74684 | 0.44945 | 0.71212 | 0.94878 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 54.6434 | 0.19672 | 42.2002 | 0.15192 | 0.5517 | 0.0019861 | 0.0069836 | 9.3874 | 0.033795 | 0.11883 | 0.079111 | 0.067397 | 284.7981 | 242.6283 | 0.0071659 | 0.0043125 | 25.7974 | 15.5249 | 0.014851 | 0.013869 | 53.4649 | 49.9289 | 8.2963 | 8.3176 | 2.8051 | 3.5998 | 1.3222 | 1.308 | 0.63639 | 0.85857 | 0.7162 | 0.93838 | 0.040582 | 0.7228 | 19.205 | 2805.1296 | 3639.5375 | 0.83496 | 1.094 | 12.7046 | 226.2772 | 0.27361 | 0.355 | 0.21873 | 0.28658 | 0.56776 | 0.39746 | 0.25812 | 0.3349 | 0.46008 | 0.65639 | 0.77027 | 0.056663 | 0.15192 | 0.11883 | 364.0605 | 308.0821
2013-11-20 | 156 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 28242.3333 | 19 | 78525.5475 | 17 | 2 | 5 | 401.2003 | 70.6054 | 180 | 2.7517 | 17 | 1250 | 15989.2207 | 2163.3077 | 90.339 | 12.5696 | 13.9824 | 37 | 25.9192 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 11.0808 | 180 | 1.4127 | 12.6935 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0757 | 486.3415 | 1169.9728 |  | 683.6314 | 11084.6582 | 3271.8978 | 1176.7639 | 0.23251 | 5.3141 | 19.6126 | 0.02 | 0.05 | 30 | 165 | 453 | 674.2003 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 453.2854 | 22.425 | 1.1246 | 1.0195 | 210.6314 | 473 | 438 | 450.575 | 223.6253 | 0.2189 | 0.027 | 1.06 | 12.3268 | 12.3268 | 674.2003 | 683.6314 | 1.1246 | 1.1271 | 2.8718 | 2.993 | 674.2003 | 683.6314 | 12.8088 | 1.1246 | 1.1271 | 298.15 | 1.9126 | 1.9933 | 674.2003 | 6.4237 | 1.1246 | 298.15 | 0.9592 | 0.99966 | 3.2719 | 4.2208 | 19.6126 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.073878 | 0.073878 | 12.8088 | 435 | 450.575 | 1.0622 | 1.067 | 298.15 | 0.32958 | 0.4006 | 0.76436 | 453 | 2816.5993 | 6.5855 | 0.65565 | 1.1329 | 21.47 | 108.559 | 0.36801 | 0.074902 | 0.074902 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 25.2949 | 52.6897 | 0.18185 | 0.078934 | 1.4379 | 25.2949 | 58.6022 | 0.20155 | 0.07992 | 1.4558 | 6.1831 | 5.113 | 1.0013 | 0.53371 | 0.65008 | 1.1443 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 51.9501 | 0.18702 | 39.8574 | 0.14349 | 5.6232 | 0.020244 | 0.07118 | 10.6709 | 0.038415 | 0.13507 | 0.08908 | 0.073663 | 320.6866 | 265.1886 | 0.0096075 | 0.005121 | 34.587 | 18.4356 | 0.016973 | 0.016513 | 61.1029 | 59.4461 | 9.455 | 9.3338 | 3.2719 | 4.4358 | 1.5121 | 1.5927 | 0.58177 | 1.059 | 0.65565 | 1.1329 | 0.078934 | 1.4379 | 19.2325 | 3271.8978 | 4220.8053 | 0.76436 | 1.3207 | 25.2949 | 460.7755 | 0.28135 | 0.36295 | 0.17656 | 0.30508 | 0.70504 | 0.13713 | 0.26543 | 0.34241 | 0.3675 | 0.66491 | 1.2692 | 0.12039 | 0.14349 | 0.13507 | 416.3765 | 343.0703
2013-12-31 | 157 | 24 | 4.2 | 50016 | 300 | 11.7 | 0.85 | 1.4 | 1.33 | 0.91 | 25827.9372 | 19 | 69172.5225 | 17 | 2 | 5 | 404.7276 | 80.9433 | 180 | 3.1763 | 17 | 1250 | 10727.869 | 1471.8842 | 55.3922 | 12.9792 | 13.9775 | 37 | 27.1846 | 20 | 10 | 5000000 | 300000 | 5000000 | 300000 | 2750000 | 300000 | 14.407 | 9.8154 | 180 | 0.99827 | 12.6803 | 659.7449 | 1.0042 | 6863.8529 | 900 | 1.1851 | 1.0713 | 468.4105 | 1126.8369 |  | 658.4265 | 10664.9427 | 2882.1884 | 1076.1641 | 0.21263 | 3.2584 | 22.4842 | 0.02 | 0.05 | 30 | 165 | 453 | 677.7276 | 2816.5993 | 125.8034 | 690.5872 | 2790.6388 | 1.0724 | 523.2322 | 25.9122 | 1.1255 | 1.0207 | 185.4265 | 473 | 438 | 447.0878 | 230.6398 | 0.2189 | 0.027 | 1.06 | 11.273 | 11.273 | 677.7276 | 658.4265 | 1.1255 | 1.1203 | 2.9139 | 2.6705 | 677.7276 | 658.4265 | 12.7956 | 1.1255 | 1.1203 | 298.15 | 1.9407 | 1.7785 | 677.7276 | 6.417 | 1.1255 | 298.15 | 0.97325 | 0.89194 | 2.8822 | 3.8011 | 22.4842 | 30 | 125.8034 | 104.83 | 0.42491 | 0.3672 | 0.084695 | 0.084695 | 12.7956 | 435 | 447.0878 | 1.0624 | 1.0662 | 298.15 | 0.32932 | 0.3839 | 0.88231 | 453 | 2816.5993 | 6.5855 | 0.75683 | 0.99714 | 21.47 | 113.8549 | 0.38565 | 0.075651 | 0.075651 | 21.47 | 37 | 154.9336 | 0.52252 | 0.081462 | 0.081462 | 15.5098 | 54.4038 | 0.18757 | 0.048575 | 1.7933 | 15.5098 | 58.5817 | 0.20149 | 0.049001 | 1.8091 | 5.4769 | 4.8014 | 0.93923 | 0.4822 | 0.75144 | 1.0071 | 0.15 | 1050000 | 0.033758 | 121.5278 | 1050000 | 0.067515 | 243.0556 | 0.045814 | 712500 | 164.9306 | 53.4965 | 0.19259 | 41.4867 | 0.14935 | 2.3369 | 0.0084128 | 0.029581 | 9.9871 | 0.035953 | 0.12642 | 0.078906 | 0.069174 | 284.0606 | 249.0281 | 0.009012 | 0.0046267 | 32.4431 | 16.6563 | 0.017285 | 0.01477 | 62.2278 | 53.1711 | 8.3591 | 8.6025 | 2.8822 | 3.3616 | 1.5568 | 1.3946 | 0.67213 | 0.91244 | 0.75683 | 0.99714 | 0.048575 | 1.7933 | 19.2126 | 2882.1884 | 3801.0898 | 0.88231 | 1.1625 | 15.5098 | 572.6011 | 0.27101 | 0.35742 | 0.22283 | 0.29358 | 0.71497 | 0.10705 | 0.25567 | 0.33718 | 0.41712 | 0.65425 | 1.7985 | 0.064182 | 0.14935 | 0.12642 | 378.7315 | 318.8555
[56 empty] | 0.21543 | [26 empty] | 11.4216 | [5 empty] | 2.7284 |  | 661.9311 | 12.7975 |  | 1.1213 |  |  | 1.8171 |  | 6.418 |  |  |  | 0.91128 |  | 3.8603 | 23.3522 | [6 empty] | 0.087965 | 12.7975 |  | 445.6804 |  | 1.0658 |  |  | 0.37786 | [5 empty] | 1.0114 |  |  |  |  | 0.076624 | [5 empty] | 0.081462 |  |  |  |  | 0.65508 |  |  |  |  | 0.67213 | 5.8232 | 4.833 | 0.70676 | 0.51576 | 0.80118 | 1.0237 | 0.15 | 1050000 | 0.033758 | 121.5278 |  |  | 243.0556 |  |  | 164.9306 |  | 0.19484 | 41.6038 | 0.14977 |  |  |  | 9.5907 | 0.034526 | 0.0098198 |  |  | 302.0192 | 250.6627 | 0.0067814 | 0.0049487 | 24.413 | 17.8154 | 0.015339 | 0.015318 | 55.2208 | 55.1443 | 8.7995 | 8.6932 | 2.9764 | 4.0441 | 1.3684 | 1.4392 | 0.71015 | 0.92348 | 0.79812 | 1.0114 | 0.26091 | 0.65508 |  |  |  |  | 1.1792 |  | 210.5943 | [7 empty] | 0.33798 |  | 0.64276 | 0.6303 |  | 0.14977 | 0.1214 | 381.6529

## INPUT PARAMETERS
| THERMODYNAMIC MODULE | [19 empty] | ECONOMIC MODULE | [93 empty] | EXERGY 10 |  |  |  |  | EXERGY 11
| Mass flow rate of fuel | Operating Hours | Mass flow rate of air | LHV | HRSG heat loss factor | HRSG blow down factor | Temperature of exhaust heat | Temp of steam | Temperature of SAC Drain | Temperature of feed water in HRSG | Mass flow rate of cooling water in SAC | Temperature of cooling water in | Temperature of cooling water out | Temperature of chilled water in | Temperature of chilled water out | Actual chilled water generated | Steam suply to SAC | Actual steam generated | Power generated | Power generated | cF(GT)(RM/GJ) | c1(RM/GJ) | Interest Rate | Number of Period | Capital Cost of GT | Salvage Cost of GT | Cost of Operation of GT | Cost of Repair of GT | Cost of Maintenance of GT | Capital Cost of HRSG | Salvage Cost of HRSG | Cost of Operation of HRSG | Cost of Repair of HRSG | Cost of Maintenance of HRSG | Capital Cost of SAC | Salvage Cost of SAC | Cost of Operation of SAC | Cost of Repair of SAC | Cost of Maintenance of SAC | Temperature of exhaust heat at HRSG stack | Ambient Temperature | m4 | T4 | m5 | T5 | Mass flow rate of feed water in HRSG | Temperature of feed water in HRSG | Mass flow rate of steam | Temperature of steam | Mass flow rate of exhaust heat at HRSG stack | T8 | Mass flow rate of chilled water | T12 | m13 | T13 | m10 | T10 | m11 | T11 |  |  | Enthalpy hs | Mass flow rate of steam | (Tg3-Tg1) | Cpg(Tg3-Tg1) | Mass flow rate of feed water in HRSG | Fuel | heat loss | Temperature of exhaust heat | Tg2 | Exhaust heat temperature leaving HRSG (T3) | Temp of steam, Ts | Enthalpy vapour, hs | Enthalpy liquid h sac drain | HRSG feed water temperature | Enthalpy of feed water by keyin Tw1 | Tw2 | Enthalpy hwTw2fluid | Enthalpy hwTw2vapor | Specific heat gas of evaporator | Zgt | Zhrsg | Zsac | Cooling water Temp in | Enthalpy Cooling water Temp in | Enthalpy Cooling water Temp out | Enthalpy hCHWin | Enthalpy hCHWout | T3 | T0 | T4 | T5 | T7 | Enthalpy (h7) | Enthalpy (h0) | Enthropy (s7) | Enthropy (s0) | CRF | T9 | Enthalpy (h9) | Enthalpy (h0) | Enthropy (s9) | Enthropy (s0) | T8 | T12 | Enthalpy (h12) | Enthalpy (h0) | Enthropy (s12) | Enthropy (s0) | T13 | Enthalpy (h13) | Enthalpy (h0) | Enthropy (s13) | Enthropy (s0) | T10 | Enthalpy (h10) | Enthalpy (h0) | Enthropy (s10) | Enthropy (s0) | T11 | Enthalpy (h11) | Enthalpy (h0) | Enthropy (s11) | Enthropy (s0) | E1 | E3 | E4 | E5 | E6 | E7 | E8 | E9 | E10 | E11 | E13 | Gas temp drop | E12 | Mass flow rate of exhaust heat | Mass flow rate of Steam | Mass flow rate of CHW | Energy Efficiency of GT | Energy Efficiency of HRSG | COP of SAC | Exergetic Efficiency of GT | Exergetic Efficiency of HRSG | Exergetic Efficiency of SAC | True Cost of Power | True Cost of CHW | Inefficientcy Cost
Days | (m3) | Hour | (kg/s) | (kJ/kg) | (%) | (%) | (Celcius) | (Celcius) | (Celcius) | (Celcius) | (kg/s) | (Celcius) | (Celcius) | (Celcius) | (Celcius) | (RTh) | (kg) | (T/h) | (kW) | (kWh) |  |  | (%) | n | (RM) | (RM) | (RM) | (RM) | (RM) | (RM) | (RM) | (RM) | (RM) | (RM) | (RM) | (RM) | (RM) | (RM) | (RM) | (Celcius) | (Celcius) | (kg/s) | Celcius | (kg/s) | Celcius | (Ton) | (Celcius) | (kg/s) | (Celcius) | (kg/s) | (Celcius) | (kg/s) | (Celcius) | (kg/s) | Celcius | (kg/s) | Celcius | (kg/s) | Celcius |  |  | (RT/kg) | (kg/s) | (Kelvin) |  | (kg/s) | (kg/s) | (%) | (Kelvin) | (Kelvin) | (Kelvin) | (Kelvin) | (kJ/kg) | (RT/kg) | (Kelvin) | (kJ/kg) | (Celcius) | (kJ/kg) | (kJ/kg) | Cpg(evap) | (RM) | (RM) | (RM) | (Kelvin) | (kJ/kg) | (kJ/kg) | (kJ/kg) | (kJ/kg) | (Kelvin) | (Kelvin) | (Kelvin) | (Kelvin) | (Kelvin) | (kJ/kg) | (kJ/kg) | (kJ/kg) | (kJ/kg) |  | (Kelvin) | (kJ/kg) | (kJ/kg) | (kJ/kg) | (kJ/kg) | (Kelvin) | (Kelvin) | (kJ/kg) | (kJ/kg) | (kJ/kg) | (kJ/kg) | (Kelvin) | (kJ/kg) | (kJ/kg) | (kJ/kg) | (kJ/kg) | (Kelvin) | (kJ/kg) | (kJ/kg) | (kJ/kg) | (kJ/kg) | (Kelvin) | (kJ/kg) | (kJ/kg) | (kJ/kg) | (kJ/kg) | [12 empty] | kW | (kg/s) | (kg/s) | (kg/s) | bar: E1 to E13
1 | 29347.8138 | 17 | 19 | 50016 | 2 | 0.05 | 398.5536 | 180 | 90 | 30 | 21.47 | 27.5778 | 37 | 11.5731 | 10.5884 | 9.4834 | 0 | 3.6977 | 74063.7775 | 4356.6928 | 14 | 14 | 10 | 5 | [15 empty] | 681.69 | 30 | 19.3411 | 671.5536 | 19.3411 | 671.5536 | 91.5532 | 30 | 1.8958 | 180 | 19.3411 | 681.69 | 5134.3423 | 10.5884 | 5134.3423 | 11.5731 | 21.47 | 27.5778 | 21.47 | 37 |  |  | 0.2189 | 1.0271 | 252.742 | 1.0247 | 1.4961 | 0.34109 | 0.02 | 671.5536 | 473 | 418.8116 | 453 | 2816.5993 | 0.0287 | 303 | 125.8034 | 165 | 690.5872 | 2790.6388 | 1.0548 | 0 | 0 | 0 | 300.5778 | 115.5007 | 154.9336 | 48.5191 | 44.3979 | 671.5536 | 303 | 671.5536 | 671.5536 | 303 | 125.8034 | 104.83 | 0.43681 | 0.3672 | 10.0001 | 453 | 2816.5993 | 104.83 | 6.5855 | 0.3672 | 691.8116 | 283.5884 | 44.3979 | 104.83 | 0.15423 | 0.3672 | 284.5731 | 48.5191 | 104.83 | 0.16796 | 0.3672 | 300.5778 | 115.5007 | 104.83 | 0.39114 | 0.3672 | 310 | 154.9336 | 104.83 | 0.52252 | 0.3672 | 17585.5972 | 2769.4413 | 1827.8312 | 941.61 | 4356.6928 | 28.2537 | 3028.6652 | 2593.744 | 73.3916 | 65.2886 | 20842.4075 | 54.1884 | 21044.925 | 19.3411 | 1.8958 | 5134.3423 | 0.25537 | 0.12524 | #DIV/0! | 0.29405 | 2.1364 | 8.1137 | 50.6367 | 11.6987 | -11156.9778
2 | 32812.0903 | 17 | 19 | 50016 | 2 | 0.05 | 408.6892 | 180 | 90 | 30 | 21.47 | 30.0356 | 37 | 12.9771 | 9.6688 | 10064.5783 | 89762.0015 | 3.7358 | 74208.8508 | 4365.2265 | 14 | 14 | 10 | 5 | [15 empty] | 681.69 | 30 | 19.3814 | 681.6892 | 19.3814 | 681.6892 | 94.5809 | 30 | 2.0016 | 180 | 19.3814 | 681.69 | 5592.4836 | 9.6688 | 5592.4836 | 12.9771 | 21.47 | 30.0356 | 21.47 | 37 |  |  | 0.2189 | 1.0377 | 265.782 | 1.0271 | 1.5456 | 0.38136 | 0.02 | 681.6892 | 473 | 415.9072 | 453 | 2816.5993 | 0.0287 | 303 | 125.8034 | 165 | 690.5872 | 2790.6388 | 1.0572 | 0 | 0 | 0 | 303.0356 | 125.7866 | 154.9336 | 54.395 | 40.5492 | 681.6892 | 303 | 681.6892 | 681.6892 | 303 | 125.8034 | 104.83 | 0.43681 | 0.3672 | 10.0001 | 453 | 2816.5993 | 104.83 | 6.5855 | 0.3672 | 688.9072 | 282.6688 | 40.5492 | 104.83 | 0.1414 | 0.3672 | 285.9771 | 54.395 | 104.83 | 0.18754 | 0.3672 | 303.0356 | 125.7866 | 104.83 | 0.42541 | 0.3672 | 310 | 154.9336 | 104.83 | 0.52252 | 0.3672 | 19661.4374 | 2904.1408 | 1916.733 | 987.4079 | 4365.2265 | 29.188 | 2997.2231 | 2620.4654 | 65.2886 | 65.2886 | 22387.683 | 57.0928 | 23128.7819 | 19.3814 | 2.0016 | 5592.4836 | 0.22886 | 0.1146 | 0.58951 | 0.2605 | 2.3982 | 8.8262 | 56.9102 | 11.9012 | 19764.3009
3 | 27419.1096 | 17 | 19 | 50016 | 2 | 0.05 | 406.7127 | 180 | 90 | 30 | 21.47 | 29.2156 | 37 | 13.2204 | 9.9739 | 9935.2567 | 91470.3446 | 3.2911 | 73638.9114 | 4331.7007 | 14 | 14 | 10 | 5 | [15 empty] | 681.69 | 30 | 19.3187 | 679.7127 | 19.3187 | 679.7127 | 81.6266 | 30 | 1.9753 | 180 | 19.3187 | 681.69 | 5512.1161 | 9.9739 | 5512.1161 | 13.2204 | 21.47 | 29.2156 | 21.47 | 37 |  |  | 0.2189 | 0.9142 | 263.238 | 1.0266 | 1.3339 | 0.31868 | 0.02 | 679.7127 | 473 | 416.4747 | 453 | 2816.5993 | 0.0287 | 303 | 125.8034 | 165 | 690.5872 | 2790.6388 | 1.0567 | 0 | 0 | 0 | 302.2156 | 122.3551 | 154.9336 | 55.4133 | 41.8264 | 679.7127 | 303 | 679.7127 | 679.7127 | 303 | 125.8034 | 104.83 | 0.43681 | 0.3672 | 10.0001 | 453 | 2816.5993 | 104.83 | 6.5855 | 0.3672 | 689.4747 | 282.9739 | 41.8264 | 104.83 | 0.14566 | 0.3672 | 286.2204 | 55.4133 | 104.83 | 0.19093 | 0.3672 | 302.2156 | 122.3551 | 104.83 | 0.41397 | 0.3672 | 310 | 154.9336 | 104.83 | 0.52252 | 0.3672 | 16429.8922 | 2869.5237 | 1893.8856 | 975.638 | 4331.7007 | 25.1903 | 2994.868 | 2308.5606 | 65.2886 | 65.2886 | 22012.235 | 56.5253 | 22729.0282 | 19.3187 | 1.9753 | 5512.1161 | 0.27177 | 0.11626 | 0.57107 | 0.31944 | 2.0739 | 9.8455 | 46.9802 | 10.12 | -33511.4703
4 | 26632.9129 | 17 | 19 | 50016 | 2 | 0.05 | 404.5658 | 180 | 90 | 30 | 21.47 | 28.6009 | 37 | 13.5005 | 11.2274 | 6478.9247 | 61873.3639 | 3.3435 | 74652.8519 | 4391.3442 | 14 | 14 | 10 | 5 | [15 empty] | 681.69 | 30 | 19.3095 | 677.5658 | 19.3095 | 677.5658 | 84.8071 | 30 | 1.9528 | 180 | 19.3095 | 681.69 | 5421.0546 | 11.2274 | 5421.0546 | 13.5005 | 21.47 | 28.6009 | 21.47 | 37 |  |  | 0.2189 | 0.92876 | 260.4753 | 1.0261 | 1.3858 | 0.30954 | 0.02 | 677.5658 | 473 | 417.0904 | 453 | 2816.5993 | 0.0287 | 303 | 125.8034 | 165 | 690.5872 | 2790.6388 | 1.0562 | 0 | 0 | 0 | 301.6009 | 119.7823 | 154.9336 | 56.5853 | 47.0722 | 677.5658 | 303 | 677.5658 | 677.5658 | 303 | 125.8034 | 104.83 | 0.43681 | 0.3672 | 10.0001 | 453 | 2816.5993 | 104.83 | 6.5855 | 0.3672 | 690.0904 | 284.2274 | 47.0722 | 104.83 | 0.16314 | 0.3672 | 286.5005 | 56.5853 | 104.83 | 0.19483 | 0.3672 | 301.6009 | 119.7823 | 104.83 | 0.4054 | 0.3672 | 310 | 154.9336 | 104.83 | 0.52252 | 0.3672 | 15958.7927 | 2840.8693 | 1874.9738 | 965.8956 | 4391.3442 | 26.1718 | 3001.4178 | 2345.3126 | 65.2886 | 65.2886 | 21587.7756 | 55.9096 | 22081.3631 | 19.3095 | 1.9528 | 5421.0546 | 0.28364 | 0.12106 | 0.55054 | 0.33476 | 2.0588 | 9.4151 | 44.9005 | 10.1182 | -39516.8631
5 | 25563.0784 | 17 | 19 | 50016 | 2 | 0.05 | 383.6577 | 180 | 90 | 30 | 21.47 | 28.2522 | 37 | 20.4722 | 16.7085 | 0 | 0 | 3.0778 | 69931.2183 | 4113.6011 | 14 | 14 | 10 | 5 | [15 empty] | 681.69 | 30 | 19.2971 | 656.6577 | 19.2971 | 656.6577 | 77.6034 | 30 | 1.7434 | 180 | 19.2971 | 681.69 | 4860.5166 | 16.7085 | 4860.5166 | 20.4722 | 21.47 | 28.2522 | 21.47 | 37 |  |  | 0.2189 | 0.85495 | 233.6026 | 1.0212 | 1.2681 | 0.29711 | 0.02 | 656.6577 | 473 | 423.0551 | 453 | 2816.5993 | 0.0287 | 303 | 125.8034 | 165 | 690.5872 | 2790.6388 | 1.0515 | 0 | 0 | 0 | 301.2522 | 118.3231 | 154.9336 | 85.763 | 70.0115 | 656.6577 | 303 | 656.6577 | 656.6577 | 303 | 125.8034 | 104.83 | 0.43681 | 0.3672 | 10.0001 | 453 | 2816.5993 | 104.83 | 6.5855 | 0.3672 | 696.0551 | 289.7085 | 70.0115 | 104.83 | 0.23957 | 0.3672 | 293.4722 | 85.763 | 104.83 | 0.29205 | 0.3672 | 301.2522 | 118.3231 | 104.83 | 0.40054 | 0.3672 | 310 | 154.9336 | 104.83 | 0.52252 | 0.3672 | 15317.7338 | 2578.2891 | 1701.6708 | 876.6183 | 4113.6011 | 23.9487 | 3076.9893 | 2158.9409 | 65.2886 | 65.2886 | 17998.2556 | 49.9449 | 18731.0108 | 19.2971 | 1.7434 | 4860.5166 | 0.27682 | 0.1182 | #DIV/0! | 0.3229 | 1.5524 | 8.676 | 46.3401 | 11.4488 | -50838.4324
6 | 26865.007 | 17 | 19 | 50016 | 2 | 0.05 | 395.3936 | 180 | 90 | 30 | 21.47 | 30.0501 | 37 | 15.99 | 12.4198 | 9465.6284 | 90952.7877 | 3.8404 | 74790.8983 | 4399.4646 | 14 | 14 | 10 | 5 | [15 empty] | 681.69 | 30 | 19.3122 | 668.3936 | 19.3122 | 668.3936 | 96.5439 | 30 | 1.8615 | 180 | 19.3122 | 681.69 | 5201.195 | 12.4198 | 5201.195 | 15.99 | 21.47 | 30.0501 | 21.47 | 37 |  |  | 0.2189 | 1.0668 | 248.6793 | 1.0239 | 1.5776 | 0.31224 | 0.02 | 668.3936 | 473 | 419.7142 | 453 | 2816.5993 | 0.0287 | 303 | 125.8034 | 165 | 690.5872 | 2790.6388 | 1.0541 | 0 | 0 | 0 | 303.0501 | 125.8476 | 154.9336 | 67.0044 | 52.0626 | 668.3936 | 303 | 668.3936 | 668.3936 | 303 | 125.8034 | 104.83 | 0.43681 | 0.3672 | 10.0001 | 453 | 2816.5993 | 104.83 | 6.5855 | 0.3672 | 692.7142 | 285.4198 | 52.0626 | 104.83 | 0.17976 | 0.3672 | 288.99 | 67.0044 | 104.83 | 0.22955 | 0.3672 | 303.0501 | 125.8476 | 104.83 | 0.42561 | 0.3672 | 310 | 154.9336 | 104.83 | 0.52252 | 0.3672 | 16097.8666 | 2725.6818 | 1798.95 | 926.7318 | 4399.4646 | 29.7938 | 3035.8708 | 2693.8548 | 65.2886 | 65.2886 | 20193.581 | 53.2858 | 20937.3936 | 19.3122 | 1.8615 | 5201.195 | 0.28171 | 0.13979 | 0.54717 | 0.329 | 2.1538 | 7.7723 | 45.5021 | 10.764 | -29899.6788
7 | 26473.5209 | 17 | 19 | 50016 | 2 | 0.05 | 402.0808 | 180 | 90 | 30 | 21.47 | 29.8968 | 37 | 13.9106 | 11.3778 | 10004.5325 | 90338.4727 | 3.2007 | 72767.4447 | 4280.4379 | 14 | 14 | 10 | 5 | [15 empty] | 681.69 | 30 | 19.3077 | 675.0808 | 19.3077 | 675.0808 | 80.1564 | 30 | 1.9278 | 180 | 19.3077 | 681.69 | 5369.6115 | 11.3778 | 5369.6115 | 13.9106 | 21.47 | 29.8968 | 21.47 | 37 |  |  | 0.2189 | 0.88908 | 257.2784 | 1.0255 | 1.3099 | 0.30769 | 0.02 | 675.0808 | 473 | 417.8024 | 453 | 2816.5993 | 0.0287 | 303 | 125.8034 | 165 | 690.5872 | 2790.6388 | 1.0556 | 0 | 0 | 0 | 302.8968 | 125.2057 | 154.9336 | 58.3018 | 47.7017 | 675.0808 | 303 | 675.0808 | 675.0808 | 303 | 125.8034 | 104.83 | 0.43681 | 0.3672 | 10.0001 | 453 | 2816.5993 | 104.83 | 6.5855 | 0.3672 | 690.8024 | 284.3778 | 47.7017 | 104.83 | 0.16523 | 0.3672 | 286.9106 | 58.3018 | 104.83 | 0.20055 | 0.3672 | 302.8968 | 125.2057 | 104.83 | 0.42347 | 0.3672 | 310 | 154.9336 | 104.83 | 0.52252 | 0.3672 | 15863.2829 | 2809.1209 | 1854.0198 | 955.1011 | 4280.4379 | 24.7366 | 3010.349 | 2245.1215 | 65.2886 | 65.2886 | 21294.7065 | 55.1976 | 21839.4716 | 19.3077 | 1.9278 | 5369.6115 | 0.27814 | 0.11679 | 0.58226 | 0.3279 | 1.9202 | 9.7275 | 45.82 | 10.169 | -43861.1744
8 | 26476.5025 | 17 | 19 | 50016 | 2 | 0.05 | 396.6236 | 180 | 90 | 30 | 21.47 | 29.9436 | 37 | 13.6019 | 10.4863 | 11102.9186 | 92544.7005 | 3.2224 | 71813.2056 | 4224.3062 | 14 | 14 | 10 | 5 | [15 empty] | 681.69 | 30 | 19.3077 | 669.6236 | 19.3077 | 669.6236 | 81.9893 | 30 | 1.8733 | 180 | 19.3077 | 681.69 | 5227.6856 | 10.4863 | 5227.6856 | 13.6019 | 21.47 | 29.9436 | 21.47 | 37 |  |  | 0.2189 | 0.89512 | 250.2605 | 1.0242 | 1.3398 | 0.30772 | 0.02 | 669.6236 | 473 | 419.363 | 453 | 2816.5993 | 0.0287 | 303 | 125.8034 | 165 | 690.5872 | 2790.6388 | 1.0544 | 0 | 0 | 0 | 302.9436 | 125.4019 | 154.9336 | 57.0099 | 43.9706 | 669.6236 | 303 | 669.6236 | 669.6236 | 303 | 125.8034 | 104.83 | 0.43681 | 0.3672 | 10.0001 | 453 | 2816.5993 | 104.83 | 6.5855 | 0.3672 | 692.363 | 283.4863 | 43.9706 | 104.83 | 0.1528 | 0.3672 | 286.6019 | 57.0099 | 104.83 | 0.19625 | 0.3672 | 302.9436 | 125.4019 | 104.83 | 0.42413 | 0.3672 | 310 | 154.9336 | 104.83 | 0.52252 | 0.3672 | 15865.0696 | 2740.4414 | 1808.6913 | 931.7501 | 4224.3062 | 25.3022 | 3030.5986 | 2260.3721 | 65.2886 | 65.2886 | 20796.499 | 53.637 | 21448.9052 | 19.3077 | 1.8733 | 5227.6856 | 0.27447 | 0.11842 | 0.63078 | 0.32186 | 1.8292 | 9.4891 | 46.585 | 10.3554 | -45653.4137
9 | 26658.2103 | 17 | 19 | 50016 | 2 | 0.05 | 403.8837 | 180 | 90 | 30 | 21.47 | 29.4617 | 37 | 13.0716 | 10.1545 | 9670.1585 | 83185.8942 | 3.7415 | 73349.7944 | 4314.6938 | 14 | 14 | 10 | 5 | [15 empty] | 681.69 | 30 | 19.3098 | 676.8837 | 19.3098 | 676.8837 | 91.5343 | 30 | 1.946 | 180 | 19.3098 | 681.69 | 5425.7565 | 10.1545 | 5425.7565 | 13.0716 | 21.47 | 29.4617 | 21.47 | 37 |  |  | 0.2189 | 1.0393 | 259.5978 | 1.0259 | 1.4958 | 0.30983 | 0.02 | 676.8837 | 473 | 417.2859 | 453 | 2816.5993 | 0.0287 | 303 | 125.8034 | 165 | 690.5872 | 2790.6388 | 1.0561 | 0 | 0 | 0 | 302.4617 | 123.3849 | 154.9336 | 54.7906 | 42.582 | 676.8837 | 303 | 676.8837 | 676.8837 | 303 | 125.8034 | 104.83 | 0.43681 | 0.3672 | 10.0001 | 453 | 2816.5993 | 104.83 | 6.5855 | 0.3672 | 690.2859 | 283.1545 | 42.582 | 104.83 | 0.14818 | 0.3672 | 286.0716 | 54.7906 | 104.83 | 0.18885 | 0.3672 | 302.4617 | 123.3849 | 104.83 | 0.4174 | 0.3672 | 310 | 154.9336 | 104.83 | 0.52252 | 0.3672 | 15973.9512 | 2832.2601 | 1869.2917 | 962.9684 | 4314.6938 | 28.2478 | 3003.9942 | 2624.5036 | 65.2886 | 65.2886 | 21699.7024 | 55.7141 | 22333.6908 | 19.3098 | 1.946 | 5425.7565 | 0.27843 | 0.1355 | 0.61119 | 0.32832 | 2.288 | 8.5097 | 45.7658 | 10.0134 | -31788.9668
10 | 26833.1196 | 17 | 19 | 50016 | 2 | 0.05 | 402.2111 | 180 | 90 | 30 | 21.47 | 29.243 | 37 | 14.0245 | 10.9552 | 9716.316 | 81585.8314 | 3.2086 | 73898.5433 | 4346.9731 | 14 | 14 | 10 | 5 | [15 empty] | 681.69 | 30 | 19.3119 | 675.2111 | 19.3119 | 675.2111 | 79.5638 | 30 | 1.9295 | 180 | 19.3119 | 681.69 | 5380.4065 | 10.9552 | 5380.4065 | 14.0245 | 21.47 | 29.243 | 21.47 | 37 |  |  | 0.2189 | 0.89127 | 257.446 | 1.0255 | 1.3002 | 0.31187 | 0.02 | 675.2111 | 473 | 417.7651 | 453 | 2816.5993 | 0.0287 | 303 | 125.8034 | 165 | 690.5872 | 2790.6388 | 1.0557 | 0 | 0 | 0 | 302.243 | 122.4695 | 154.9336 | 58.7784 | 45.9334 | 675.2111 | 303 | 675.2111 | 675.2111 | 303 | 125.8034 | 104.83 | 0.43681 | 0.3672 | 10.0001 | 453 | 2816.5993 | 104.83 | 6.5855 | 0.3672 | 690.7651 | 283.9552 | 45.9334 | 104.83 | 0.15934 | 0.3672 | 287.0245 | 58.7784 | 104.83 | 0.20214 | 0.3672 | 302.243 | 122.4695 | 104.83 | 0.41435 | 0.3672 | 310 | 154.9336 | 104.83 | 0.52252 | 0.3672 | 16078.7593 | 2811.376 | 1855.5082 | 955.8679 | 4346.9731 | 24.5537 | 3010.5173 | 2250.6584 | 65.2886 | 65.2886 | 21312.971 | 55.2349 | 21974.4372 | 19.3119 | 1.9295 | 5380.4065 | 0.27868 | 0.11587 | 0.62615 | 0.32764 | 1.9273 | 9.7636 | 45.8079 | 10.2438 | -41676.1029
11 | 27531.029 | 17 | 19 | 50016 | 2 | 0.05 | 409.1781 | 180 | 90 | 30 | 21.47 | 29.4483 | 37 | 13.8189 | 10.6445 | 9928.8215 | 81839.1541 | 3.3314 | 74469.0322 | 4380.5313 | 14 | 14 | 10 | 5 | [15 empty] | 681.69 | 30 | 19.32 | 682.1781 | 19.32 | 682.1781 | 82.8307 | 30 | 2.0002 | 180 | 19.32 | 681.69 | 5582.5737 | 10.6445 | 5582.5737 | 13.8189 | 21.47 | 29.4483 | 21.47 | 37 |  |  | 0.2189 | 0.92538 | 266.4113 | 1.0272 | 1.3536 | 0.31998 | 0.02 | 682.1781 | 473 | 415.7668 | 453 | 2816.5993 | 0.0287 | 303 | 125.8034 | 165 | 690.5872 | 2790.6388 | 1.0573 | 0 | 0 | 0 | 302.4483 | 123.3291 | 154.9336 | 57.918 | 44.633 | 682.1781 | 303 | 682.1781 | 682.1781 | 303 | 125.8034 | 104.83 | 0.43681 | 0.3672 | 10.0001 | 453 | 2816.5993 | 104.83 | 6.5855 | 0.3672 | 688.7668 | 283.6445 | 44.633 | 104.83 | 0.15501 | 0.3672 | 286.8189 | 57.918 | 104.83 | 0.19927 | 0.3672 | 302.4483 | 123.3291 | 104.83 | 0.41722 | 0.3672 | 310 | 154.9336 | 104.83 | 0.52252 | 0.3672 | 16496.9558 | 2901.1955 | 1914.789 | 986.4065 | 4380.5313 | 25.5619 | 2985.916 | 2336.779 | 65.2886 | 65.2886 | 22159.773 | 57.2332 | 22869.5991 | 19.32 | 2.0002 | 5582.5737 | 0.27371 | 0.11695 | 0.63786 | 0.3222 | 2.1577 | 9.7868 | 46.604 | 10.0989 | -30354.5235
12 | 27119.0188 | 17 | 19 | 50016 | 2 | 0.05 | 409.9513 | 180 | 90 | 30 | 21.47 | 28.8446 | 37 | 18.6332 | 16.6371 | 0 | 442.7708 | 3.794 | 73806.7831 | 4341.5755 | 14 | 14 | 10 | 5 | [15 empty] | 681.69 | 30 | 19.3152 | 682.9513 | 19.3152 | 682.9513 | 93.6341 | 30 | 2.0074 | 180 | 19.3152 | 681.69 | 5566.3952 | 16.6371 | 5566.3952 | 18.6332 | 21.47 | 28.8446 | 21.47 | 37 |  |  | 0.2189 | 1.0539 | 267.4066 | 1.0274 | 1.5301 | 0.31519 | 0.02 | 682.9513 | 473 | 415.5447 | 453 | 2816.5993 | 0.0287 | 303 | 125.8034 | 165 | 690.5872 | 2790.6388 | 1.0575 | 0 | 0 | 0 | 301.8446 | 120.8025 | 154.9336 | 78.0664 | 69.7126 | 682.9513 | 303 | 682.9513 | 682.9513 | 303 | 125.8034 | 104.83 | 0.43681 | 0.3672 | 10.0001 | 453 | 2816.5993 | 104.83 | 6.5855 | 0.3672 | 688.5447 | 289.6371 | 69.7126 | 104.83 | 0.23857 | 0.3672 | 291.6332 | 78.0664 | 104.83 | 0.26641 | 0.3672 | 301.8446 | 120.8025 | 104.83 | 0.4088 | 0.3672 | 310 | 154.9336 | 104.83 | 0.52252 | 0.3672 | 16250.0738 | 2910.3704 | 1920.8445 | 989.5259 | 4341.5755 | 28.8958 | 2982.3061 | 2661.2865 | 65.2886 | 65.2886 | 21022.1326 | 57.4553 | 21467.1887 | 19.3152 | 2.0074 | 5566.3952 | 0.2754 | 0.13458 | 0 | 0.32546 | 2.48 | 8.0665 | 46.2065 | 10.5976 | -18174.1164
13 | 27966.3507 | 17 | 19 | 50016 | 2 | 0.05 | 373.7094 | 180 | 90 | 30 | 21.47 | 29.1429 | 37 | 17.5347 | 14.9956 | 4891.7404 | 45135.3389 | 3.1122 | 78690.2667 | 4628.8392 | 14 | 14 | 10 | 5 | [15 empty] | 681.69 | 30 | 19.325 | 646.7094 | 19.325 | 646.7094 | 76.8385 | 30 | 1.6474 | 180 | 19.325 | 681.69 | 4573.6624 | 14.9956 | 4573.6624 | 17.5347 | 21.47 | 29.1429 | 21.47 | 37 |  |  | 0.2189 | 0.8645 | 220.8367 | 1.019 | 1.2556 | 0.32504 | 0.02 | 646.7094 | 473 | 425.8728 | 453 | 2816.5993 | 0.0287 | 303 | 125.8034 | 165 | 690.5872 | 2790.6388 | 1.0493 | 0 | 0 | 0 | 302.1429 | 122.0506 | 154.9336 | 73.4689 | 62.8426 | 646.7094 | 303 | 646.7094 | 646.7094 | 303 | 125.8034 | 104.83 | 0.43681 | 0.3672 | 10.0001 | 453 | 2816.5993 | 104.83 | 6.5855 | 0.3672 | 698.8728 | 287.9956 | 62.8426 | 104.83 | 0.21568 | 0.3672 | 290.5347 | 73.4689 | 104.83 | 0.25109 | 0.3672 | 302.1429 | 122.0506 | 104.83 | 0.41296 | 0.3672 | 310 | 154.9336 | 104.83 | 0.52252 | 0.3672 | 16757.8062 | 2460.9655 | 1624.2372 | 836.7283 | 4628.8392 | 23.7127 | 3118.3519 | 2183.0577 | 65.2886 | 65.2886 | 17474.2139 | 47.1272 | 17939.3728 | 19.325 | 1.6474 | 4573.6624 | 0.28473 | 0.11289 | 0.56982 | 0.32377 | 1.4452 | 8.2175 | 45.7717 | 13.0779 | -42505.3987
14 | 31161.2827 | 17 | 19 | 50016 | 2 | 0.05 | 410.6665 | 180 | 90 | 30 | 21.47 | 29.2937 | 37 | 15.8408 | 12.2758 | 9762.0578 | 85995.4818 | 3.3033 | 78486.9933 | 4616.882 | 14 | 14 | 10 | 5 | [15 empty] | 681.69 | 30 | 19.3622 | 683.6665 | 19.3622 | 683.6665 | 84.8012 | 30 | 2.0195 | 180 | 19.3622 | 681.69 | 5641.7364 | 12.2758 | 5641.7364 | 15.8408 | 21.47 | 29.2937 | 21.47 | 37 |  |  | 0.2189 | 0.91759 | 268.3274 | 1.0276 | 1.3858 | 0.36217 | 0.02 | 683.6665 | 473 | 415.3391 | 453 | 2816.5993 | 0.0287 | 303 | 125.8034 | 165 | 690.5872 | 2790.6388 | 1.0576 | 0 | 0 | 0 | 302.2937 | 122.6816 | 154.9336 | 66.38 | 51.46 | 683.6665 | 303 | 683.6665 | 683.6665 | 303 | 125.8034 | 104.83 | 0.43681 | 0.3672 | 10.0001 | 453 | 2816.5993 | 104.83 | 6.5855 | 0.3672 | 688.3391 | 285.2758 | 51.46 | 104.83 | 0.17776 | 0.3672 | 288.8408 | 66.38 | 104.83 | 0.22747 | 0.3672 | 302.2937 | 122.6816 | 104.83 | 0.41506 | 0.3672 | 310 | 154.9336 | 104.83 | 0.52252 | 0.3672 | 18672.2517 | 2926.6351 | 1931.5791 | 995.0559 | 4616.882 | 26.17 | 2986.8987 | 2317.1098 | 65.2886 | 65.2886 | 21937.6941 | 57.6609 | 22743.3282 | 19.3622 | 2.0195 | 5641.7364 | 0.25487 | 0.10528 | 0.59684 | 0.29322 | 2.1708 | 9.8154 | 50.7636 | 11.494 | -1441.7711
15 | 27920.7102 | 17 | 19 | 50016 | 2 | 0.05 | 403.4981 | 180 | 90 | 30 | 21.47 | 29.4379 | 37 | 14.3478 | 11.0827 | 10074.7349 | 92029.2989 | 3.2403 | 78284.2589 | 4604.9564 | 14 | 14 | 10 | 5 | [15 empty] | 681.69 | 30 | 19.3245 | 676.4981 | 19.3245 | 676.4981 | 80.8841 | 30 | 1.9437 | 180 | 19.3245 | 681.69 | 5424.7988 | 11.0827 | 5424.7988 | 14.3478 | 21.47 | 29.4379 | 21.47 | 37 |  |  | 0.2189 | 0.90008 | 259.1017 | 1.0258 | 1.3217 | 0.32451 | 0.02 | 676.4981 | 473 | 417.3964 | 453 | 2816.5993 | 0.0287 | 303 | 125.8034 | 165 | 690.5872 | 2790.6388 | 1.056 | 0 | 0 | 0 | 302.4379 | 123.2853 | 154.9336 | 60.1316 | 46.4668 | 676.4981 | 303 | 676.4981 | 676.4981 | 303 | 125.8034 | 104.83 | 0.43681 | 0.3672 | 10.0001 | 453 | 2816.5993 | 104.83 | 6.5855 | 0.3672 | 690.3964 | 284.0827 | 46.4668 | 104.83 | 0.16112 | 0.3672 | 287.3478 | 60.1316 | 104.83 | 0.20665 | 0.3672 | 302.4379 | 123.2853 | 104.83 | 0.41707 | 0.3672 | 310 | 154.9336 | 104.83 | 0.52252 | 0.3672 | 16730.4579 | 2829.5211 | 1867.4839 | 962.0372 | 4604.9564 | 24.9611 | 3007.7087 | 2272.9005 | 65.2886 | 65.2886 | 21418.5635 | 55.6036 | 22128.0466 | 19.3245 | 1.9437 | 5424.7988 | 0.28372 | 0.11335 | 0.57557 | 0.33127 | 1.9715 | 9.7356 | 45.1865 | 10.585 | -34699.761
16 | 28257.6749 | 17 | 19 | 50016 | 2 | 0.05 | 400.0546 | 180 | 90 | 30 | 21.47 | 29.6149 | 37 | 14.9101 | 11.3346 | 10583.8519 | 89326.0852 | 3.1114 | 79704.4494 | 4688.497 | 14 | 14 | 10 | 5 | [15 empty] | 681.69 | 30 | 19.3284 | 673.0546 | 19.3284 | 673.0546 | 78.5103 | 30 | 1.9096 | 180 | 19.3284 | 681.69 | 5334.2015 | 11.3346 | 5334.2015 | 14.9101 | 21.47 | 29.6149 | 21.47 | 37 |  |  | 0.2189 | 0.86429 | 254.6723 | 1.025 | 1.283 | 0.32842 | 0.02 | 673.0546 | 473 | 418.3823 | 453 | 2816.5993 | 0.0287 | 303 | 125.8034 | 165 | 690.5872 | 2790.6388 | 1.0552 | 0 | 0 | 0 | 302.6149 | 124.0263 | 154.9336 | 62.485 | 47.5211 | 673.0546 | 303 | 673.0546 | 673.0546 | 303 | 125.8034 | 104.83 | 0.43681 | 0.3672 | 10.0001 | 453 | 2816.5993 | 104.83 | 6.5855 | 0.3672 | 691.3823 | 284.3346 | 47.5211 | 104.83 | 0.16463 | 0.3672 | 287.9101 | 62.485 | 104.83 | 0.21449 | 0.3672 | 302.6149 | 124.0263 | 104.83 | 0.41954 | 0.3672 | 310 | 154.9336 | 104.83 | 0.52252 | 0.3672 | 16932.3715 | 2786.5375 | 1839.1147 | 947.4227 | 4688.497 | 24.2286 | 3021.1071 | 2182.5254 | 65.2886 | 65.2886 | 20940.712 | 54.6177 | 21704.6708 | 19.3284 | 1.9096 | 5334.2015 | 0.28542 | 0.10831 | 0.62295 | 0.33144 | 1.826 | 9.9448 | 45.0689 | 10.9218 | -37572.198
17 | 27991.9369 | 17 | 19 | 50016 | 2 | 0.05 | 399.1233 | 180 | 90 | 30 | 21.47 | 29.0322 | 37 | 14.5551 | 11.1615 | 10818.3546 | 90489.2439 | 3.2244 | 79189.9583 | 4658.2328 | 14 | 14 | 10 | 5 | [15 empty] | 681.69 | 30 | 19.3253 | 672.1233 | 19.3253 | 672.1233 | 80.9992 | 30 | 1.9 | 180 | 19.3253 | 681.69 | 5301.0538 | 11.1615 | 5301.0538 | 14.5551 | 21.47 | 29.0322 | 21.47 | 37 |  |  | 0.2189 | 0.89566 | 253.4746 | 1.0248 | 1.3236 | 0.32534 | 0.02 | 672.1233 | 473 | 418.6487 | 453 | 2816.5993 | 0.0287 | 303 | 125.8034 | 165 | 690.5872 | 2790.6388 | 1.055 | 0 | 0 | 0 | 302.0322 | 121.5874 | 154.9336 | 60.9994 | 46.7965 | 672.1233 | 303 | 672.1233 | 672.1233 | 303 | 125.8034 | 104.83 | 0.43681 | 0.3672 | 10.0001 | 453 | 2816.5993 | 104.83 | 6.5855 | 0.3672 | 691.6487 | 284.1615 | 46.7965 | 104.83 | 0.16222 | 0.3672 | 287.5551 | 60.9994 | 104.83 | 0.20954 | 0.3672 | 302.0322 | 121.5874 | 104.83 | 0.41142 | 0.3672 | 310 | 154.9336 | 104.83 | 0.52252 | 0.3672 | 16773.1379 | 2774.356 | 1831.075 | 943.281 | 4658.2328 | 24.9967 | 3024.0822 | 2261.7274 | 65.2886 | 65.2886 | 20885.9567 | 54.3513 | 21606.5538 | 19.3253 | 1.9 | 5301.0538 | 0.28627 | 0.11319 | 0.62857 | 0.33276 | 1.8749 | 9.5531 | 44.9073 | 10.8682 | -36996.5328
18 | 27838.2344 | 17 | 19 | 50016 | 2 | 0.05 | 403.5732 | 180 | 90 | 30 | 21.47 | 28.2415 | 37 | 14.0343 | 11.1044 | 9291.462 | 78457.8676 | 3.3986 | 76807.3792 | 4518.0811 | 14 | 14 | 10 | 5 | [15 empty] | 681.69 | 30 | 19.3235 | 676.5732 | 19.3235 | 676.5732 | 85.3194 | 30 | 1.9443 | 180 | 19.3235 | 681.69 | 5412.1875 | 11.1044 | 5412.1875 | 14.0343 | 21.47 | 28.2415 | 21.47 | 37 |  |  | 0.2189 | 0.94404 | 259.1983 | 1.0258 | 1.3942 | 0.32355 | 0.02 | 676.5732 | 473 | 417.3749 | 453 | 2816.5993 | 0.0287 | 303 | 125.8034 | 165 | 690.5872 | 2790.6388 | 1.056 | 0 | 0 | 0 | 301.2415 | 118.2782 | 154.9336 | 58.8195 | 46.5577 | 676.5732 | 303 | 676.5732 | 676.5732 | 303 | 125.8034 | 104.83 | 0.43681 | 0.3672 | 10.0001 | 453 | 2816.5993 | 104.83 | 6.5855 | 0.3672 | 690.3749 | 284.1044 | 46.5577 | 104.83 | 0.16142 | 0.3672 | 287.0343 | 58.8195 | 104.83 | 0.20228 | 0.3672 | 301.2415 | 118.2782 | 104.83 | 0.40039 | 0.3672 | 310 | 154.9336 | 104.83 | 0.52252 | 0.3672 | 16681.0373 | 2830.3324 | 1868.0194 | 962.313 | 4518.0811 | 26.3299 | 3007.2808 | 2383.9157 | 65.2886 | 65.2886 | 21436.734 | 55.6251 | 22071.8946 | 19.3235 | 1.9443 | 5412.1875 | 0.27919 | 0.11914 | 0.62264 | 0.3262 | 2.0694 | 9.2587 | 45.9005 | 10.5806 | -30443.6096
19 | 25149.11 | 17 | 19 | 50016 | 2 | 0.05 | 403.9186 | 180 | 90 | 30 | 21.47 | 28.6239 | 37 | 12.9744 | 10.1275 | 8808.4682 | 83485.8086 | 3.6129 | 66977.0644 | 3939.8273 | 14 | 14 | 10 | 5 | [15 empty] | 681.69 | 30 | 19.2923 | 676.9186 | 19.2923 | 676.9186 | 90.1232 | 30 | 1.9446 | 180 | 19.2923 | 681.69 | 5414.0726 | 10.1275 | 5414.0726 | 12.9744 | 21.47 | 28.6239 | 21.47 | 37 |  |  | 0.2189 | 1.0036 | 259.6427 | 1.0259 | 1.4727 | 0.29229 | 0.02 | 676.9186 | 473 | 417.2759 | 453 | 2816.5993 | 0.0287 | 303 | 125.8034 | 165 | 690.5872 | 2790.6388 | 1.0561 | 0 | 0 | 0 | 301.6239 | 119.8787 | 154.9336 | 54.3836 | 42.4693 | 676.9186 | 303 | 676.9186 | 676.9186 | 303 | 125.8034 | 104.83 | 0.43681 | 0.3672 | 10.0001 | 453 | 2816.5993 | 104.83 | 6.5855 | 0.3672 | 690.2759 | 283.1275 | 42.4693 | 104.83 | 0.1478 | 0.3672 | 285.9744 | 54.3836 | 104.83 | 0.1875 | 0.3672 | 301.6239 | 119.8787 | 104.83 | 0.40572 | 0.3672 | 310 | 154.9336 | 104.83 | 0.52252 | 0.3672 | 15069.6785 | 2830.1298 | 1867.8857 | 962.2441 | 3939.8273 | 27.8124 | 3001.1362 | 2534.2873 | 65.2886 | 65.2886 | 21674.0612 | 55.7241 | 22291.4367 | 19.2923 | 1.9446 | 5414.0726 | 0.26949 | 0.13667 | 0.55472 | 0.32189 | 2.2118 | 8.7959 | 46.912 | 9.4644 | -41199.0273
20 | 25473.4726 | 17 | 19 | 50016 | 2 | 0.05 | 387.9566 | 180 | 90 | 30 | 21.47 | 29.0813 | 37 | 18.1146 | 16.862 | 0 | 0 | 3.2503 | 68825.3175 | 4048.5481 | 14 | 14 | 10 | 5 | [15 empty] | 681.69 | 30 | 19.2961 | 660.9566 | 19.2961 | 660.9566 | 79.7931 | 30 | 1.7859 | 180 | 19.2961 | 681.69 | 4894.5233 | 16.862 | 4894.5233 | 18.1146 | 21.47 | 29.0813 | 21.47 | 37 |  |  | 0.2189 | 0.90285 | 239.1231 | 1.0222 | 1.3039 | 0.29606 | 0.02 | 660.9566 | 473 | 421.8335 | 453 | 2816.5993 | 0.0287 | 303 | 125.8034 | 165 | 690.5872 | 2790.6388 | 1.0524 | 0 | 0 | 0 | 302.0813 | 121.7928 | 154.9336 | 75.896 | 70.6538 | 660.9566 | 303 | 660.9566 | 660.9566 | 303 | 125.8034 | 104.83 | 0.43681 | 0.3672 | 10.0001 | 453 | 2816.5993 | 104.83 | 6.5855 | 0.3672 | 694.8335 | 289.862 | 70.6538 | 104.83 | 0.24171 | 0.3672 | 291.1146 | 75.896 | 104.83 | 0.25918 | 0.3672 | 302.0813 | 121.7928 | 104.83 | 0.4121 | 0.3672 | 310 | 154.9336 | 104.83 | 0.52252 | 0.3672 | 15264.0408 | 2631.0244 | 1736.4761 | 894.5483 | 4048.5481 | 24.6245 | 3060.8931 | 2279.9033 | 65.2886 | 65.2886 | 18586.4047 | 51.1665 | 18831.9767 | 19.2961 | 1.7859 | 4894.5233 | 0.2734 | 0.12443 | #DIV/0! | 0.32047 | 1.7028 | 8.26 | 46.7787 | 11.3475 | -45370.3042
21 | 28123.831 | 17 | 19 | 50016 | 2 | 0.05 | 399.6848 | 180 | 90 | 30 | 21.47 | 30.0542 | 37 | 15.9671 | 12.7193 | 9564.1512 | 90556.5651 | 3.1707 | 78884.5436 | 4640.2673 | 14 | 14 | 10 | 5 | [15 empty] | 681.69 | 30 | 19.3269 | 672.6848 | 19.3269 | 672.6848 | 81.6715 | 30 | 1.9057 | 180 | 19.3269 | 681.69 | 5321.7844 | 12.7193 | 5321.7844 | 15.9671 | 21.47 | 30.0542 | 21.47 | 37 |  |  | 0.2189 | 0.88076 | 254.1967 | 1.0249 | 1.3346 | 0.32687 | 0.02 | 672.6848 | 473 | 418.4881 | 453 | 2816.5993 | 0.0287 | 303 | 125.8034 | 165 | 690.5872 | 2790.6388 | 1.0551 | 0 | 0 | 0 | 303.0542 | 125.8646 | 154.9336 | 66.9087 | 53.316 | 672.6848 | 303 | 672.6848 | 672.6848 | 303 | 125.8034 | 104.83 | 0.43681 | 0.3672 | 10.0001 | 453 | 2816.5993 | 104.83 | 6.5855 | 0.3672 | 691.4881 | 285.7193 | 53.316 | 104.83 | 0.18394 | 0.3672 | 288.9671 | 66.9087 | 104.83 | 0.22923 | 0.3672 | 303.0542 | 125.8646 | 104.83 | 0.42567 | 0.3672 | 310 | 154.9336 | 104.83 | 0.52252 | 0.3672 | 16852.1705 | 2781.651 | 1835.8897 | 945.7613 | 4640.2673 | 25.2042 | 3022.237 | 2224.1126 | 65.2886 | 65.2886 | 20666.6431 | 54.5119 | 21358.9839 | 19.3269 | 1.9057 | 5321.7844 | 0.28383 | 0.11083 | 0.55529 | 0.32979 | 1.8535 | 9.6034 | 45.3051 | 11.046 | -35119.4159
22 | 28545.5461 | 17 | 19 | 50016 | 2 | 0.05 | 403.3186 | 180 | 90 | 30 | 21.47 | 29.2266 | 37 | 14.2322 | 11.1868 | 9197.2582 | 90541.377 | 3.2128 | 78773.9408 | 4633.7612 | 14 | 14 | 10 | 5 | [15 empty] | 681.69 | 30 | 19.3318 | 676.3186 | 19.3318 | 676.3186 | 81.8112 | 30 | 1.9426 | 180 | 19.3318 | 681.69 | 5416.7121 | 11.1868 | 5416.7121 | 14.2322 | 21.47 | 29.2266 | 21.47 | 37 |  |  | 0.2189 | 0.89244 | 258.8707 | 1.0258 | 1.3369 | 0.33177 | 0.02 | 676.3186 | 473 | 417.4479 | 453 | 2816.5993 | 0.0287 | 303 | 125.8034 | 165 | 690.5872 | 2790.6388 | 1.0559 | 0 | 0 | 0 | 302.2266 | 122.4012 | 154.9336 | 59.6477 | 46.9024 | 676.3186 | 303 | 676.3186 | 676.3186 | 303 | 125.8034 | 104.83 | 0.43681 | 0.3672 | 10.0001 | 453 | 2816.5993 | 104.83 | 6.5855 | 0.3672 | 690.4479 | 284.1868 | 46.9024 | 104.83 | 0.16257 | 0.3672 | 287.2322 | 59.6477 | 104.83 | 0.20504 | 0.3672 | 302.2266 | 122.4012 | 104.83 | 0.41413 | 0.3672 | 310 | 154.9336 | 104.83 | 0.52252 | 0.3672 | 17104.8678 | 2828.3068 | 1866.6825 | 961.6243 | 4633.7612 | 25.2473 | 3009.506 | 2253.5978 | 65.2886 | 65.2886 | 21411.7207 | 55.5521 | 22072.4767 | 19.3318 | 1.9426 | 5416.7121 | 0.27925 | 0.11052 | 0.53407 | 0.32457 | 1.9499 | 9.7943 | 46.0392 | 10.8492 | -30742.6238
23 | 28225.9995 | 17 | 19 | 50016 | 2 | 0.05 | 402.7138 | 180 | 90 | 30 | 21.47 | 28.8957 | 37 | 14.1707 | 10.8548 | 8774.117 | 89425.6327 | 3.1315 | 76888.3347 | 4522.8432 | 14 | 14 | 10 | 5 | [15 empty] | 681.69 | 30 | 19.3281 | 675.7138 | 19.3281 | 675.7138 | 78.6819 | 30 | 1.9362 | 180 | 19.3281 | 681.69 | 5400.9288 | 10.8548 | 5400.9288 | 14.1707 | 21.47 | 28.8957 | 21.47 | 37 |  |  | 0.2189 | 0.86986 | 258.0927 | 1.0256 | 1.2858 | 0.32806 | 0.02 | 675.7138 | 473 | 417.6211 | 453 | 2816.5993 | 0.0287 | 303 | 125.8034 | 165 | 690.5872 | 2790.6388 | 1.0558 | 0 | 0 | 0 | 301.8957 | 121.0162 | 154.9336 | 59.3906 | 45.513 | 675.7138 | 303 | 675.7138 | 675.7138 | 303 | 125.8034 | 104.83 | 0.43681 | 0.3672 | 10.0001 | 453 | 2816.5993 | 104.83 | 6.5855 | 0.3672 | 690.6211 | 283.8548 | 45.513 | 104.83 | 0.15794 | 0.3672 | 287.1707 | 59.3906 | 104.83 | 0.20418 | 0.3672 | 301.8957 | 121.0162 | 104.83 | 0.40951 | 0.3672 | 310 | 154.9336 | 104.83 | 0.52252 | 0.3672 | 16913.3913 | 2820.0984 | 1861.2649 | 958.8335 | 4522.8432 | 24.2815 | 3011.174 | 2196.5829 | 65.2886 | 65.2886 | 21362.6222 | 55.3789 | 22079.9842 | 19.3281 | 1.9362 | 5400.9288 | 0.27565 | 0.10874 | 0.51586 | 0.32092 | 1.8891 | 10.052 | 46.5923 | 10.7241 | -34408.3129
24 | 27159.8774 | 17 | 19 | 50016 | 2 | 0.05 | 407.9641 | 180 | 90 | 30 | 21.47 | 28.0569 | 37 | 18.6662 | 17.3636 | 0 | 0 | 3.7348 | 73954 | 4350.2353 | 14 | 14 | 10 | 5 | [15 empty] | 681.69 | 30 | 19.3157 | 680.9641 | 19.3157 | 680.9641 | 91.431 | 30 | 1.9875 | 180 | 19.3157 | 681.69 | 5450.6756 | 17.3636 | 5450.6756 | 18.6662 | 21.47 | 28.0569 | 21.47 | 37 |  |  | 0.2189 | 1.0374 | 264.8486 | 1.0269 | 1.4941 | 0.31566 | 0.02 | 680.9641 | 473 | 416.1155 | 453 | 2816.5993 | 0.0287 | 303 | 125.8034 | 165 | 690.5872 | 2790.6388 | 1.057 | 0 | 0 | 0 | 301.0569 | 117.5057 | 154.9336 | 78.2046 | 72.753 | 680.9641 | 303 | 680.9641 | 680.9641 | 303 | 125.8034 | 104.83 | 0.43681 | 0.3672 | 10.0001 | 453 | 2816.5993 | 104.83 | 6.5855 | 0.3672 | 689.1155 | 290.3636 | 72.753 | 104.83 | 0.2487 | 0.3672 | 291.6662 | 78.2046 | 104.83 | 0.26687 | 0.3672 | 301.0569 | 117.5057 | 104.83 | 0.39782 | 0.3672 | 310 | 154.9336 | 104.83 | 0.52252 | 0.3672 | 16274.5568 | 2885.0351 | 1904.1232 | 980.9119 | 4350.2353 | 28.216 | 2989.7559 | 2619.7839 | 65.2886 | 65.2886 | 20577.8943 | 56.8845 | 20862.293 | 19.3157 | 1.9875 | 5450.6756 | 0.27554 | 0.13267 | #DIV/0! | 0.3249 | 2.3871 | 7.9634 | 46.2472 | 10.9213 | -18399.4482
25 | 25929.7009 | 17 | 19 | 50016 | 2 | 0.05 | 398.7097 | 180 | 90 | 30 | 21.47 | 29.014 | 37 | 15.6287 | 12.5136 | 8766.3667 | 79553.0144 | 3.1134 | 69939.1892 | 4114.07 | 14 | 14 | 10 | 5 | [15 empty] | 681.69 | 30 | 19.3014 | 671.7097 | 19.3014 | 671.7097 | 79.989 | 30 | 1.8935 | 180 | 19.3014 | 681.69 | 5278.155 | 12.5136 | 5278.155 | 15.6287 | 21.47 | 29.014 | 21.47 | 37 |  |  | 0.2189 | 0.86484 | 252.9428 | 1.0247 | 1.3071 | 0.30137 | 0.02 | 671.7097 | 473 | 418.7669 | 453 | 2816.5993 | 0.0287 | 303 | 125.8034 | 165 | 690.5872 | 2790.6388 | 1.0549 | 0 | 0 | 0 | 302.014 | 121.5113 | 154.9336 | 65.4924 | 52.4553 | 671.7097 | 303 | 671.7097 | 671.7097 | 303 | 125.8034 | 104.83 | 0.43681 | 0.3672 | 10.0001 | 453 | 2816.5993 | 104.83 | 6.5855 | 0.3672 | 691.7669 | 285.5136 | 52.4553 | 104.83 | 0.18107 | 0.3672 | 288.6287 | 65.4924 | 104.83 | 0.22451 | 0.3672 | 302.014 | 121.5113 | 104.83 | 0.41116 | 0.3672 | 310 | 154.9336 | 104.83 | 0.52252 | 0.3672 | 15537.4189 | 2765.7149 | 1825.3718 | 940.3431 | 4114.07 | 24.6849 | 3021.8653 | 2183.9114 | 65.2886 | 65.2886 | 20568.7607 | 54.2331 | 21227.3584 | 19.3014 | 1.8935 | 5278.155 | 0.27294 | 0.11592 | 0.57937 | 0.32212 | 1.8046 | 9.7199 | 46.6615 | 10.2473 | -47924.3908
26 | 20788.4636 | 17 | 19 | 50016 | 2 | 0.05 | 326.0912 | 180 | 90 | 30 | 21.47 | 28.3092 | 37 | 17.6479 | 16.2204 | 0 | 0 | 2.3916 | 55817.1522 | 3283.3619 | 14 | 14 | 10 | 5 | [15 empty] | 681.69 | 30 | 19.2416 | 599.0912 | 19.2416 | 599.0912 | 53.9461 | 30 | 1.1772 | 180 | 19.2416 | 681.69 | 3184.9514 | 16.2204 | 3184.9514 | 17.6479 | 21.47 | 28.3092 | 21.47 | 37 |  |  | 0.2189 | 0.66433 | 159.9128 | 1.0092 | 0.88154 | 0.24161 | 0.02 | 599.0912 | 473 | 439.1784 | 453 | 2816.5993 | 0.0287 | 303 | 125.8034 | 165 | 690.5872 | 2790.6388 | 1.039 | 0 | 0 | 0 | 301.3092 | 118.5618 | 154.9336 | 73.9428 | 67.9686 | 599.0912 | 303 | 599.0912 | 599.0912 | 303 | 125.8034 | 104.83 | 0.43681 | 0.3672 | 10.0001 | 453 | 2816.5993 | 104.83 | 6.5855 | 0.3672 | 712.1784 | 289.2204 | 67.9686 | 104.83 | 0.23276 | 0.3672 | 290.6479 | 73.9428 | 104.83 | 0.25267 | 0.3672 | 301.3092 | 118.5618 | 104.83 | 0.40133 | 0.3672 | 310 | 154.9336 | 104.83 | 0.52252 | 0.3672 | 12456.7216 | 1903.1052 | 1256.0495 | 647.0558 | 3283.3619 | 16.648 | 3280.5061 | 1677.5781 | 65.2886 | 65.2886 | 12154.0346 | 33.8216 | 12336.1486 | 19.2416 | 1.1772 | 3184.9514 | 0.2717 | 0.11768 | #DIV/0! | 0.31111 | 0.82043 | 7.3535 | 47.7588 | 14.1368 | -101182.6339
27 | 287.405 | 17 | 19 | 50016 | 2 | 0.05 | 118.011 | 180 | 90 | 30 | 21.47 | 29.8219 | 37 | 15.2393 | 11.563 | 8422.5788 | 90192.2222 | 0.035794 | 0 | 0 | 14 | 14 | 10 | 5 | [15 empty] | 681.69 | 30 | 19.0033 | 391.011 | 19.0033 | 391.011 | 0.4543 | 30 | -0.72076 | 180 | 19.0033 | 681.69 | -2072.0184 | 11.563 | -2072.0184 | 15.2393 | 21.47 | 29.8219 | 21.47 | 37 |  |  | 0.2189 | 0.0099429 | -102.9568 | 0.98742 | 0.0074238 | 0.0033404 | 0.02 | 391.011 | 473 | 493.9678 | 453 | 2816.5993 | 0.0287 | 303 | 125.8034 | 165 | 690.5872 | 2790.6388 | 1.0034 | 0 | 0 | 0 | 302.8219 | 124.8924 | 154.9336 | 63.8627 | 48.4768 | 391.011 | 303 | 391.011 | 391.011 | 303 | 125.8034 | 104.83 | 0.43681 | 0.3672 | 10.0001 | 453 | 2816.5993 | 104.83 | 6.5855 | 0.3672 | 766.9678 | 284.563 | 48.4768 | 104.83 | 0.16782 | 0.3672 | 288.2393 | 63.8627 | 104.83 | 0.21908 | 0.3672 | 302.8219 | 124.8924 | 104.83 | 0.42243 | 0.3672 | 310 | 154.9336 | 104.83 | 0.52252 | 0.3672 | 172.2169 | 215.0424 | 141.928 | 73.1144 | 0 | 0.1402 | 3988.5029 | 25.108 | 65.2886 | 65.2886 | -8106.8923 | -20.9678 | -8412.0149 | 19.0033 | -0.72076 | -2072.0184 | 0 | -0.01516 | 0.49098 | 0 | 0.0064909 | -335.0328 | #DIV/0! | -0.28662 | 11383661.0054
28 | 17402.6467 | 17 | 19 | 50016 | 2 | 0.05 | 250.5611 | 180 | 90 | 30 | 21.47 | 28.2358 | 37 | 15.0178 | 13.9721 | 1614.3662 | 15175.7774 | 1.9162 | 40170.9417 | 2362.9966 | 14 | 14 | 10 | 5 | [15 empty] | 681.69 | 30 | 19.2023 | 523.5611 | 19.2023 | 523.5611 | 47.1968 | 30 | 0.46274 | 180 | 19.2023 | 681.69 | 1123.4099 | 13.9721 | 1123.4099 | 15.0178 | 21.47 | 28.2358 | 21.47 | 37 |  |  | 0.2189 | 0.53229 | 63.8833 | 0.99716 | 0.77125 | 0.20226 | 0.02 | 523.5611 | 473 | 459.6778 | 453 | 2816.5993 | 0.0287 | 303 | 125.8034 | 165 | 690.5872 | 2790.6388 | 1.0243 | 0 | 0 | 0 | 301.2358 | 118.2543 | 154.9336 | 62.9356 | 58.5594 | 523.5611 | 303 | 523.5611 | 523.5611 | 303 | 125.8034 | 104.83 | 0.43681 | 0.3672 | 10.0001 | 453 | 2816.5993 | 104.83 | 6.5855 | 0.3672 | 732.6778 | 286.9721 | 58.5594 | 104.83 | 0.20141 | 0.3672 | 288.0178 | 62.9356 | 104.83 | 0.21599 | 0.3672 | 301.2358 | 118.2543 | 104.83 | 0.40031 | 0.3672 | 310 | 154.9336 | 104.83 | 0.52252 | 0.3672 | 10427.8955 | 1142.6897 | 754.1752 | 388.5145 | 2362.9966 | 14.5651 | 3550.3775 | 1344.1398 | 65.2886 | 65.2886 | 4405.3747 | 13.3222 | 4452.4287 | 19.2023 | 0.46274 | 1123.4099 | 0.23358 | 0.12631 | 0.55929 | 0.25449 | 0.47549 | 3.3125 | 57.3137 | 32.789 | -58724.9113
29 | 27485.6641 | 17 | 19 | 50016 | 2 | 0.05 | 399.5737 | 180 | 90 | 30 | 21.47 | 29.7149 | 37 | 15.7361 | 12.493 | 9600.797 | 79552.5643 | 3.0568 | 78350.5869 | 4608.8581 | 14 | 14 | 10 | 5 | [15 empty] | 681.69 | 30 | 19.3195 | 672.5737 | 19.3195 | 672.5737 | 79.9503 | 30 | 1.9039 | 180 | 19.3195 | 681.69 | 5314.2834 | 12.493 | 5314.2834 | 15.7361 | 21.47 | 29.7149 | 21.47 | 37 |  |  | 0.2189 | 0.84911 | 254.0539 | 1.0249 | 1.3065 | 0.31945 | 0.02 | 672.5737 | 473 | 418.5198 | 453 | 2816.5993 | 0.0287 | 303 | 125.8034 | 165 | 690.5872 | 2790.6388 | 1.0551 | 0 | 0 | 0 | 302.7149 | 124.4446 | 154.9336 | 65.9418 | 52.3691 | 672.5737 | 303 | 672.5737 | 672.5737 | 303 | 125.8034 | 104.83 | 0.43681 | 0.3672 | 10.0001 | 453 | 2816.5993 | 104.83 | 6.5855 | 0.3672 | 691.5198 | 285.493 | 52.3691 | 104.83 | 0.18079 | 0.3672 | 288.7361 | 65.9418 | 104.83 | 0.22601 | 0.3672 | 302.7149 | 124.4446 | 104.83 | 0.42094 | 0.3672 | 310 | 154.9336 | 104.83 | 0.52252 | 0.3672 | 16469.7725 | 2779.1839 | 1834.2614 | 944.9225 | 4608.8581 | 24.673 | 3021.4894 | 2144.1839 | 65.2886 | 65.2886 | 20686.6929 | 54.4802 | 21377.0416 | 19.3195 | 1.9039 | 5314.2834 | 0.28846 | 0.10876 | 0.63452 | 0.33664 | 1.7853 | 9.9698 | 44.4573 | 10.7862 | -43356.4272
30 | 27477.4267 | 17 | 19 | 50016 | 2 | 0.05 | 400.8171 | 180 | 90 | 30 | 21.47 | 28.7763 | 37 | 13.9998 | 11.0516 | 10010.0696 | 81364.982 | 3.2183 | 79398.5419 | 4670.5025 | 14 | 14 | 10 | 5 | [15 empty] | 681.69 | 30 | 19.3194 | 673.8171 | 19.3194 | 673.8171 | 81.4993 | 30 | 1.9163 | 180 | 19.3194 | 681.69 | 5337.6108 | 11.0516 | 5337.6108 | 13.9998 | 21.47 | 28.7763 | 21.47 | 37 |  |  | 0.2189 | 0.89397 | 255.6529 | 1.0252 | 1.3318 | 0.31936 | 0.02 | 673.8171 | 473 | 418.1641 | 453 | 2816.5993 | 0.0287 | 303 | 125.8034 | 165 | 690.5872 | 2790.6388 | 1.0554 | 0 | 0 | 0 | 301.7763 | 120.5164 | 154.9336 | 58.6753 | 46.3365 | 673.8171 | 303 | 673.8171 | 673.8171 | 303 | 125.8034 | 104.83 | 0.43681 | 0.3672 | 10.0001 | 453 | 2816.5993 | 104.83 | 6.5855 | 0.3672 | 691.1641 | 284.0516 | 46.3365 | 104.83 | 0.16069 | 0.3672 | 286.9998 | 58.6753 | 104.83 | 0.2018 | 0.3672 | 301.7763 | 120.5164 | 104.83 | 0.40785 | 0.3672 | 310 | 154.9336 | 104.83 | 0.52252 | 0.3672 | 16464.8365 | 2794.8497 | 1844.6008 | 950.2489 | 4670.5025 | 25.151 | 3016.8593 | 2257.4675 | 65.2886 | 65.2886 | 21148.7177 | 54.8359 | 21779.0605 | 19.3194 | 1.9163 | 5337.6108 | 0.2924 | 0.11435 | 0.64683 | 0.34166 | 1.9043 | 9.6476 | 43.8247 | 10.5839 | -41198.3568
31 | 27477.8217 | 17 | 19 | 50016 | 2 | 0.05 | 403.3537 | 180 | 90 | 30 | 21.47 | 29.0793 | 37 | 14.2596 | 11.0928 | 10565.3227 | 85115.6922 | 3.2552 | 80339.9175 | 4725.8775 | 14 | 14 | 10 | 5 | [15 empty] | 681.69 | 30 | 19.3194 | 676.3537 | 19.3194 | 676.3537 | 82.0882 | 30 | 1.9417 | 180 | 19.3194 | 681.69 | 5415.2923 | 11.0928 | 5415.2923 | 14.2596 | 21.47 | 29.0793 | 21.47 | 37 |  |  | 0.2189 | 0.90422 | 258.9159 | 1.0258 | 1.3414 | 0.31936 | 0.02 | 676.3537 | 473 | 417.4378 | 453 | 2816.5993 | 0.0287 | 303 | 125.8034 | 165 | 690.5872 | 2790.6388 | 1.0559 | 0 | 0 | 0 | 302.0793 | 121.7844 | 154.9336 | 59.7624 | 46.5091 | 676.3537 | 303 | 676.3537 | 676.3537 | 303 | 125.8034 | 104.83 | 0.43681 | 0.3672 | 10.0001 | 453 | 2816.5993 | 104.83 | 6.5855 | 0.3672 | 690.4378 | 284.0928 | 46.5091 | 104.83 | 0.16126 | 0.3672 | 287.2596 | 59.7624 | 104.83 | 0.20542 | 0.3672 | 302.0793 | 121.7844 | 104.83 | 0.41207 | 0.3672 | 310 | 154.9336 | 104.83 | 0.52252 | 0.3672 | 16465.0732 | 2826.9368 | 1865.7783 | 961.1585 | 4725.8775 | 25.3327 | 3007.4436 | 2283.3484 | 65.2886 | 65.2886 | 21400.1659 | 55.5622 | 22087.0755 | 19.3194 | 1.9417 | 5415.2923 | 0.29586 | 0.11529 | 0.65262 | 0.34652 | 1.9778 | 9.6731 | 43.2491 | 10.4365 | -39743.3422
29.104
[60 empty] | 273 | 273 | 273

## hliquid1
Temp | h
28.96 | 121.46
36.16 | 151.53
41.51 | 173.88
45.81 | 191.83
60.06 | 251.4
69.17 | 289.23
75.87 | 317.58
81.33 | 340.49
85.94 | 359.86
89.95 | 376.7
101.3347 | 424.1827
108.5817 | 454.5075
115.8287 | 484.8324
123.0758 | 515.1572
130.3228 | 545.4821
137.5698 | 575.8069 | New X | Interpolated Value
144.8168 | 606.1318 | 170 | 710.569 | <-- using cell references
152.0639 | 636.4566 | 175 | 731.4228 | <-- using named ranges
159.3109 | 666.7815 | 180 | 753.354 |  | KnownX | blue cells
166.5579 | 697.1063 | 185 | 773.1304 |  | KnownY | green cells
173.805 | 727.4312 | 159 | 664.6907
181.052 | 757.756
188.299 | 788.0808
195.5461 | 818.4057
202.7931 | 848.7305
210.0401 | 879.0554
217.2872 | 909.3802
224.5342 | 939.7051
231.7812 | 970.0299
239.0282 | 1000.3548
246.2753 | 1030.6796
253.5223 | 1061.0045
260.7693 | 1091.3293
268.0164 | 1121.6542
275.2634 | 1151.979
282.5104 | 1182.3039
289.7575 | 1212.6287
297.0045 | 1242.9536
304.2515 | 1273.2784
311.4985 | 1303.6033
318.7456 | 1333.9281
325.9926 | 1364.253
333.2396 | 1394.5778
340.4867 | 1424.9027
347.7337 | 1455.2275
354.9807 | 1485.5524
362.2278 | 1515.8772
369.4748 | 1546.2021
376.7218 | 1576.5269
383.9688 | 1606.8518

## hvapour1
Temp | h
28.96 | 2554.4
36.16 | 2567.4
41.51 | 2577
45.81 | 2584.7
60.06 | 2609.7
69.17 | 2625.3
75.87 | 2636.8
81.33 | 2645.9
85.94 | 2653.5
89.95 | 2660
101.3347 | 2680.4533
108.5817 | 2692.9958
115.8287 | 2705.5382
123.0758 | 2718.0806
130.3228 | 2730.623
137.5698 | 2743.1655 | New X | Interpolated Value
144.8168 | 2755.7079 | 170 | 2803.8153 | <-- using cell references
152.0639 | 2768.2503 | 175 | 2812.7981 | <-- using named ranges
159.3109 | 2780.7927 | 180 | 2816.5993 |  | KnownX | blue cells
166.5579 | 2793.3352 | 185 | 2830.7638 |  | KnownY | green cells
173.805 | 2805.8776 | 194 | 2846.933
181.052 | 2818.42
188.299 | 2830.9624
195.5461 | 2843.5048
202.7931 | 2856.0473
210.0401 | 2868.5897
217.2872 | 2881.1321
224.5342 | 2893.6745
231.7812 | 2906.217
239.0282 | 2918.7594
246.2753 | 2931.3018
253.5223 | 2943.8442
260.7693 | 2956.3867
268.0164 | 2968.9291
275.2634 | 2981.4715
282.5104 | 2994.0139
289.7575 | 3006.5564
297.0045 | 3019.0988
304.2515 | 3031.6412
311.4985 | 3044.1836
318.7456 | 3056.7261
325.9926 | 3069.2685
333.2396 | 3081.8109
340.4867 | 3094.3533
347.7337 | 3106.8958
354.9807 | 3119.4382
362.2278 | 3131.9806
369.4748 | 3144.523
376.7218 | 3157.0655
383.9688 | 3169.6079

## sliquid1
Temp | h
28.96 | 0.4226
36.16 | 0.521
41.51 | 0.5926
45.81 | 0.6493
60.06 | 0.832
69.17 | 0.9439
75.87 | 1.0259
81.33 | 1.091
85.94 | 1.1453
89.95 | 1.1919
93.5 | 1.2329
96.71 | 1.2695
99.63 | 1.3026
111.4 | 1.4336
120.2 | 1.5301
127.4 | 1.6072 | New X | Interpolated Value
133.6 | 1.6718 | 170 | 2.1164 | <-- using cell references
138.9 | 1.7275 | 175 | 2.1742 | <-- using named ranges
143.6 | 1.7766 | 180 | 2.2319 |  | KnownX | blue cells
147.9 | 1.8207 | 185 | 2.2897 |  | KnownY | green cells
151.9 | 1.8607 | 127 | 1.6198
158.9 | 1.9312
165 | 1.9922
170.4 | 2.0462
175.4 | 2.0946
179.9 | 2.1387
198.3 | 2.315
212.4 | 2.4474
224 | 2.5547
233.9 | 2.6457
242.6 | 2.7253
250.4 | 2.7964
257.5 | 2.861
264 | 2.9202
275.6 | 3.0267
285.9 | 3.1211
295.1 | 3.2068
303.4 | 3.2858
311.1 | 3.3596
318.2 | 3.4295
324.8 | 3.4962
330.9 | 3.5605
336.8 | 3.6232
342.2 | 3.6848
347.4 | 3.7461
352.4 | 3.8079
357.1 | 3.8715
361.5 | 3.9388
365.8 | 4.0139
374.1 | 4.4298

## svapour1
Temp | h
28.96 | 8.4746
36.16 | 8.3304
41.51 | 8.2287
45.81 | 8.1502
60.06 | 7.9085
69.17 | 7.7686
75.87 | 7.67
81.33 | 7.5939
85.94 | 7.532
89.95 | 7.4797
93.5 | 7.4346
96.71 | 7.3946
99.63 | 7.3594
111.4 | 7.2233
120.2 | 7.1271
127.4 | 7.0527 | New X | Interpolated Value
133.6 | 6.9919 | 170 | 6.4627 | <-- using cell references
138.9 | 6.9405 | 175 | 6.3992 | <-- using named ranges
143.6 | 6.8959 | 180 | 6.5855 |  | KnownX | blue cells
147.9 | 6.8565 | 185 | 6.2722 |  | KnownY | green cells
151.9 | 6.8212 | 194 | 6.1578
158.9 | 6.76
165 | 6.708
170.4 | 6.6628
175.4 | 6.6226
179.9 | 6.5863
198.3 | 6.4448
212.4 | 6.3409
224 | 6.2575
233.9 | 6.1869
242.6 | 6.1253
250.4 | 6.0701
257.5 | 6.0199
264 | 5.9734
275.6 | 5.8892
285.9 | 5.8133
295.1 | 5.7432
303.4 | 5.6772
311.1 | 5.6141
318.2 | 5.5527
324.8 | 5.4924
330.9 | 5.4323
336.8 | 5.3717
342.2 | 5.3098
347.4 | 5.2455
352.4 | 5.1777
357.1 | 5.1044
361.5 | 5.0228
365.8 | 4.9269
374.1 | 4.4298

## h-SAC
tem | sf
5 | 0.0763
50 | 0.7038
75 | 1.0158
100 | 1.3072
125 | 1.5816
150 | 1.8418
175 | 2.0906
200 | 2.3305
|  | New X | Interpolated Value
<-- using cell references
<-- using named ranges
|  | 11 | 0.15997 |  | KnownX1 | blue cells
[5 empty] | KnownY1 | green cells
tem | hf
5 | 21.01
50 | 209.34
75 | 314.03
100 | 419.17
125 | 525.07
150 | 632.18
175 | 741.02
200 | 852.26
|  | New X | Interpolated Value
|  | 9 | 37.7504